## FCI
Campo FCI = .24
0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.25 | 0.26 | 0.27 | 0.28 | 0.29 | 0.3 | 0.31 | 0.32 | 0.33 | 0.34 | 0.35 | 0.36 | 0.37 | 0.38 | 0.39 | 0.4 | 0.41 | 0.42 | 0.43 | 0.44 | 0.45 | 0.46 | 0.47 | 0.48 | 0.49 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.59 | 0.6 | 0.61 | 0.62 | 0.63 | 0.64 | 0.65 | 0.66 | 0.67 | 0.68 | 0.69 | 0.7 | 0.71 | 0.72 | 0.73 | 0.74 | 0.75 | 0.76 | 0.77 | 0.78 | 0.79 | 0.8 | 0.81 | 0.82 | 0.83 | 0.84 | 0.85 | 0.86 | 0.87 | 0.88 | 0.89 | 0.9 | 0.91 | 0.92 | 0.93 | 0.94 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99 | 1
Good | [8 empty] | Fair | [15 empty] | Poor | [24 empty] | 0.51: Critical
0 | [5 empty] | 0.1 | [16 empty] | 0.25 | [24 empty] | 0.5 | bar: 0.96
Clover Flat FCI = .14
0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.25 | 0.26 | 0.27 | 0.28 | 0.29 | 0.3 | 0.31 | 0.32 | 0.33 | 0.34 | 0.35 | 0.36 | 0.37 | 0.38 | 0.39 | 0.4 | 0.41 | 0.42 | 0.43 | 0.44 | 0.45 | 0.46 | 0.47 | 0.48 | 0.49 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.59 | 0.6 | 0.61 | 0.62 | 0.63 | 0.64 | 0.65 | 0.66 | 0.67 | 0.68 | 0.69 | 0.7 | 0.71 | 0.72 | 0.73 | 0.74 | 0.75 | 0.76 | 0.77 | 0.78 | 0.79 | 0.8 | 0.81 | 0.82 | 0.83 | 0.84 | 0.85 | 0.86 | 0.87 | 0.88 | 0.89 | 0.9 | 0.91 | 0.92 | 0.93 | 0.94 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99 | 1
Good | [8 empty] | Fair | [15 empty] | Poor | [24 empty] | 0.51: Critical
0 | [5 empty] | 0.1 | [16 empty] | 0.25 | [24 empty] | 0.5 | bar: 0.96
Descanso FCI=0.20
0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.25 | 0.26 | 0.27 | 0.28 | 0.29 | 0.3 | 0.31 | 0.32 | 0.33 | 0.34 | 0.35 | 0.36 | 0.37 | 0.38 | 0.39 | 0.4 | 0.41 | 0.42 | 0.43 | 0.44 | 0.45 | 0.46 | 0.47 | 0.48 | 0.49 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.59 | 0.6 | 0.61 | 0.62 | 0.63 | 0.64 | 0.65 | 0.66 | 0.67 | 0.68 | 0.69 | 0.7 | 0.71 | 0.72 | 0.73 | 0.74 | 0.75 | 0.76 | 0.77 | 0.78 | 0.79 | 0.8 | 0.81 | 0.82 | 0.83 | 0.84 | 0.85 | 0.86 | 0.87 | 0.88 | 0.89 | 0.9 | 0.91 | 0.92 | 0.93 | 0.94 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99 | 1
Good | [8 empty] | Fair | [15 empty] | Poor | [24 empty] | 0.51: Critical
0 | [5 empty] | 0.1 | [16 empty] | 0.25 | [24 empty] | 0.5 | bar: 0.96
Jacumba FCI = .29
0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.25 | 0.26 | 0.27 | 0.28 | 0.29 | 0.3 | 0.31 | 0.32 | 0.33 | 0.34 | 0.35 | 0.36 | 0.37 | 0.38 | 0.39 | 0.4 | 0.41 | 0.42 | 0.43 | 0.44 | 0.45 | 0.46 | 0.47 | 0.48 | 0.49 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.59 | 0.6 | 0.61 | 0.62 | 0.63 | 0.64 | 0.65 | 0.66 | 0.67 | 0.68 | 0.69 | 0.7 | 0.71 | 0.72 | 0.73 | 0.74 | 0.75 | 0.76 | 0.77 | 0.78 | 0.79 | 0.8 | 0.81 | 0.82 | 0.83 | 0.84 | 0.85 | 0.86 | 0.87 | 0.88 | 0.89 | 0.9 | 0.91 | 0.92 | 0.93 | 0.94 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99 | 1
Good | [8 empty] | Fair | [15 empty] | Poor | [24 empty] | 0.51: Critical
0 | [5 empty] | 0.1 | [16 empty] | 0.25 | [24 empty] | 0.5 | bar: 0.96
Mountain Empire High School FCI = .28
0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.25 | 0.26 | 0.27 | 0.28 | 0.29 | 0.3 | 0.31 | 0.32 | 0.33 | 0.34 | 0.35 | 0.36 | 0.37 | 0.38 | 0.39 | 0.4 | 0.41 | 0.42 | 0.43 | 0.44 | 0.45 | 0.46 | 0.47 | 0.48 | 0.49 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.59 | 0.6 | 0.61 | 0.62 | 0.63 | 0.64 | 0.65 | 0.66 | 0.67 | 0.68 | 0.69 | 0.7 | 0.71 | 0.72 | 0.73 | 0.74 | 0.75 | 0.76 | 0.77 | 0.78 | 0.79 | 0.8 | 0.81 | 0.82 | 0.83 | 0.84 | 0.85 | 0.86 | 0.87 | 0.88 | 0.89 | 0.9 | 0.91 | 0.92 | 0.93 | 0.94 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99 | 1
Good | [8 empty] | Fair | [15 empty] | Poor | [24 empty] | 0.51: Critical
0 | [5 empty] | 0.1 | [16 empty] | 0.25 | [24 empty] | 0.5 | bar: 0.96
Pine Valley Middle School FCI = .25
0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.25 | 0.26 | 0.27 | 0.28 | 0.29 | 0.3 | 0.31 | 0.32 | 0.33 | 0.34 | 0.35 | 0.36 | 0.37 | 0.38 | 0.39 | 0.4 | 0.41 | 0.42 | 0.43 | 0.44 | 0.45 | 0.46 | 0.47 | 0.48 | 0.49 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.59 | 0.6 | 0.61 | 0.62 | 0.63 | 0.64 | 0.65 | 0.66 | 0.67 | 0.68 | 0.69 | 0.7 | 0.71 | 0.72 | 0.73 | 0.74 | 0.75 | 0.76 | 0.77 | 0.78 | 0.79 | 0.8 | 0.81 | 0.82 | 0.83 | 0.84 | 0.85 | 0.86 | 0.87 | 0.88 | 0.89 | 0.9 | 0.91 | 0.92 | 0.93 | 0.94 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99 | 1
Good | [8 empty] | Fair | [15 empty] | Poor | [24 empty] | 0.51: Critical
0 | [5 empty] | 0.1 | [16 empty] | 0.25 | [24 empty] | 0.5 | bar: 0.96
Potrero Elementary School FCI = .21
0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.25 | 0.26 | 0.27 | 0.28 | 0.29 | 0.3 | 0.31 | 0.32 | 0.33 | 0.34 | 0.35 | 0.36 | 0.37 | 0.38 | 0.39 | 0.4 | 0.41 | 0.42 | 0.43 | 0.44 | 0.45 | 0.46 | 0.47 | 0.48 | 0.49 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.59 | 0.6 | 0.61 | 0.62 | 0.63 | 0.64 | 0.65 | 0.66 | 0.67 | 0.68 | 0.69 | 0.7 | 0.71 | 0.72 | 0.73 | 0.74 | 0.75 | 0.76 | 0.77 | 0.78 | 0.79 | 0.8 | 0.81 | 0.82 | 0.83 | 0.84 | 0.85 | 0.86 | 0.87 | 0.88 | 0.89 | 0.9 | 0.91 | 0.92 | 0.93 | 0.94 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99 | 1
Good | [8 empty] | Fair | [15 empty] | Poor | [24 empty] | 0.51: Critical
0 | [5 empty] | 0.1 | [16 empty] | 0.25 | [24 empty] | 0.5 | bar: 0.96

## Enrollment
[7 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
|  |  | Loading | Classrooms | SPED | Empty | 2014 | 2013 | 2012 | 2011 | 2010 | 2009 | 2008 | 2007 | 2006 | 2005
| Descanso | K | 24 | 6 | 1 |  | 42 | 49 | 47 | 0 | 0 | 0 | 12 | 16 | 28 | 20
7 | 175 | 1 | 24 |  |  |  | 21 | 30 | 30 | 0 | 0 | 0 | 16 | 21 | 19 | 17
|  | 2 | 24 |  |  |  | 33 | 29 | 33 | 0 | 0 | 0 | 21 | 15 | 24 | 20
|  | 3 | 24 |  |  |  | 31 | 35 | 28 | 0 | 0 | 0 | 16 | 21 | 21 | 28
|  | 4 | 30 | 3 |  |  | 35 | 29 | 28 | 25 | 29 | 26 | 20 | 18 | 29 | 25
|  | 5 | 30 |  |  |  | 24 | 27 | 25 | 26 | 25 | 32 | 15 | 30 | 25 | 16
|  | 6 | 30 | [5 empty] | 0 | 22 | 25 | 27 | 29 | 23 | 17 | 25
0 | 0 | 7 | 35 |  |  |  | 3: 2; 4: 20; 5: 16; 6: 29
|  | 8 | 35 |  |  |  | 3: 3; 4: 18; 5: 29; 6: 0
|  | 9 | 35
|  | 10 | 35
|  | 11 | 35
1 | 15 | 12 | 35
190 | Total |  | 249 | 234 | 15 |  | 186 | 199 | 196 | 111 | 124 | 114 | 129 | 144 | 163 | 151
| Jacumba | K | 24 | [6 empty] | 20 | 30 | 31 | 22 | 18 | 23 | 14
1 | 25 | 1 | 24 | [6 empty] | 23 | 27 | 27 | 17 | 23 | 21 | 19
|  | 2 | 24 |  |  |  | 6: 8; 7: 11; 8: 17; 9: 8; 10: 16
|  | 3 | 24
|  | 4 | 30
|  | 5 | 30
|  | 6 | 30 | 1 |  |  | 1: 22; 2: 19; 3: 25
2 | 54 | 7 | 35 | 2 |  |  | 1: 18; 2: 20; 3: 17
|  | 8 | 35 |  |  |  | 1: 21; 2: 15; 3: 16
|  | 9 | 35
|  | 10 | 35
|  | 11 | 35
0 | 0 | 12 | 35
79 | Total |  | 100 | 100 |  |  | 61 | 54 | 58 | 43 | 57 | 66 | 50 | 58 | 52 | 49
| Clover | K | 24 | 4 | 1 |  | 41 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 150 | 1 | 24 |  |  |  | 19 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2 | 24 |  |  |  | 15 | 19 | 26 | 24 | 23 | 5 | 11 | 4 | 14 | 7
|  | 3 | 24 |  |  |  | 21 | 27 | 24 | 24 | 22 | 18 | 18 | 25 | 24 | 26
|  | 4 | 30 | 2 |  |  | 24 | 21 | 22 | 22 | 24 | 31 | 19 | 20 | 21 | 15
|  | 5 | 30 |  |  |  | 18 | 23 | 22 | 24 | 25 | 16 | 18 | 17 | 17 | 32
|  | 6 | 30 | [5 empty] | 1 | 23 | 20 | 21 | 18 | 19 | 26 | 34
0 | 0 | 7 | 35 |  |  |  | 3: 0; 4: 19; 5: 24; 6: 13
|  | 8 | 35 |  |  |  | 3: 1; 4: 22; 5: 22
|  | 9 | 35 | bar: 3
|  | 10 | 35
|  | 11 | 35
1 | 15 | 12 | 35
165 | Total |  | 171 | 156 | 15 |  | 138 | 149 | 155 | 158 | 160 | 104 | 84 | 85 | 102 | 114
| Campo | K | 24 | 6 | 1 | 8 | 68 | 62 | 52 | 55 | 58 | 68 | 62 | 35 | 41 | 45
9 | 225 | 1 | 24 |  |  |  | 39 | 34 | 59 | 56 | 43 | 51 | 34 | 44 | 51 | 37
|  | 2 | 24 |  |  |  | 30 | 60 | 56 | 45 | 49 | 42 | 43 | 52 | 38 | 49
|  | 3 | 24 |  |  |  | 53 | 61 | 47 | 51 | 30 | 36 | 53 | 43 | 54 | 42
|  | 4 | 30 | 5 |  |  | 60 | 40 | 54 | 31 | 41 | 52 | 54 | 55 | 42 | 44
|  | 5 | 30 |  |  |  | 38 | 47 | 33 | 41 | 52 | 58 | 69 | 37 | 46 | 57
|  | 6 | 30 |  |  |  | 44 | 33 | 36 | 42 | 49 | 61 | 42 | 44 | 58 | 40
2 | 54 | 7 | 35 | 2 |  |  | 32 | 34 | 39 | 52 | 50 | 26
|  | 8 | 35 |  |  |  | 1: 31; 2: 41; 3: 46; 4: 47; 5: 27
|  | 9 | 35
|  | 10 | 35
|  | 11 | 35
1 | 15 | 12 | 35
294 | Total |  | 579 | 364 | 15 | 200 | 395 | 412 | 422 | 420 | 399 | 394 | 357 | 310 | 330 | 314
| MEHS | K | 24 |  | 1
0 | 0 | 1 | 24
|  | 2 | 24
|  | 3 | 24
|  | 4 | 30
|  | 5 | 30
|  | 6 | 30
24 | 648 | 7 | 35
|  | 8 | 35
|  | 9 | 35 | 31 |  |  | 110 | 88 | 98 | 111 | 115 | 135 | 117 | 118 | 136 | 145
|  | 10 | 35 |  |  |  | 86 | 114 | 101 | 118 | 128 | 94 | 111 | 138 | 128 | 115
|  | 11 | 35 |  |  |  | 101 | 93 | 105 | 122 | 80 | 119 | 136 | 121 | 114 | 119
1 | 15 | 12 | 35 |  |  |  | 95 | 97 | 112 | 83 | 84 | 9 | 89 | 101 | 96 | 99
663 | Total |  | 1100 | 1085 | 15 |  | 392 | 392 | 416 | 434 | 407 | 357 | 453 | 478 | 474 | 478
| Potrero | K | 24 | 5 | 2 | 4 | 31 | 34 | 31 | 26 | 20 | 41 | 23 | 19 | 19 | 24
8 | 200 | 1 | 24 |  |  |  | 31 | 25 | 26 | 21 | 29 | 23 | 20 | 24 | 21 | 19
|  | 2 | 24 |  |  |  | 26 | 28 | 27 | 33 | 24 | 33 | 29 | 21 | 23 | 27
|  | 3 | 24 |  |  |  | 28 | 23 | 28 | 27 | 31 | 29 | 22 | 24 | 28 | 20
|  | 4 | 30 | 3 |  |  | 26 | 34 | 24 | 27 | 32 | 25 | 25 | 27 | 20 | 23
|  | 5 | 30 |  |  |  | 32 | 27 | 27 | 37 | 24 | 27 | 28 | 20 | 24 | 29
|  | 6 | 30 |  |  |  | 29 | 27 | 34 | 29 | 25 | 21 | 18 | 22 | 32 | 25
2 | 54 | 7 | 35 | 2 |  |  | 32 | 31 | 32 | 28 | 27 | 9
|  | 8 | 35 |  |  |  | 1: 32; 2: 29; 3: 32; 4: 30; 5: 24
|  | 9 | 35
|  | 10 | 35
|  | 11 | 35
2 | 30 | 12 | 35
284 | Total |  | 410 | 280 | 30 | 100 | 267 | 258 | 261 | 258 | 236 | 208 | 165 | 157 | 167 | 167
| Ald Ed | K | 24
0 | 0 | 1 | 24
|  | 2 | 24
|  | 3 | 24
|  | 4 | 30
|  | 5 | 30
|  | 6 | 30
1 | 27 | 7 | 35
|  | 8 | 35
|  | 9 | 35 | 1 |  |  | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 1 | 6 | 4
|  | 10 | 35 |  |  |  | 6 | 6 | 1 | 7 | 8 | 5 | 1 | 1 | 1 | 2
|  | 11 | 35 |  |  |  | 9 | 8 | 9 | 11 | 16 | 8 | 0 | 0 | 2 | 0
1 | 15 | 12 | 35 |  |  |  | 4 | 7 | 18 | 15 | 12 | 4 | 0 | 1 | 0 | 0
42 | Total |  |  | 35 |  |  | 20 | 23 | 28 | 33 | 36 | 18 | 1 | 3 | 9 | 6
| Pine Valley | K | 24 | [6 empty] | 33 | 28 | 34 | 10 | 7 | 12 | 10
2 | 50 | 1 | 24 | [6 empty] | 28 | 30 | 22 | 8 | 11 | 9 | 10
|  | 2 | 24 | [6 empty] | 28 | 25 | 25 | 9 | 6 | 9 | 15
|  | 3 | 24 | [6 empty] | 25 | 25 | 27 | 8 | 11 | 12 | 15
|  | 4 | 30 |  |  |  | 7: 8; 8: 13; 9: 14; 10: 19
|  | 5 | 30 |  |  |  | 7: 11; 8: 20; 9: 18; 10: 27
|  | 6 | 30 | 2 |  |  | 19 | 21 | 21 |  |  |  | 18 | 16 | 20 | 16
4 | 108 | 7 | 35 | 4 |  |  | 1: 26; 2: 18; 3: 17
|  | 8 | 35 |  |  |  | 1: 16; 2: 23; 3: 16
|  | 9 | 35
|  | 10 | 35
|  | 11 | 35
0 | 0 | 12 | 35
158 | Total |  |  | 200 |  |  | 61 | 62 | 54 | 114 | 108 | 108 | 72 | 84 | 94 | 112
[7 empty] | 1520 | 1549 | 1590 | 1571 | 1527 | 1369 | 1311 | 1319 | 1391 | 1391
| 2014 | 2013 | 2012 | 2011 | 2010 | 2009 | 1: 2008; 2: 2007; 3: 2006; 4: 2005; 7: loading
k | 182 | 185 | 168 | 134 | 136 | 174 | 129 | 95 | 123 | 113 |  | Tk-3 | 24
1 | 110 | 108 | 135 | 128 | 129 | 123 | 95 | 123 | 121 | 102 |  | gr 4-6 | 30
2 | 104 | 136 | 142 | 130 | 121 | 113 | 124 | 115 | 116 | 134 |  | gr 7-12 | 35
3 | 133 | 146 | 127 | 127 | 108 | 110 | 1: 117; 2: 124; 3: 139; 4: 131
4 | 145 | 124 | 128 | 105 | 126 | 134 | 126 | 133 | 126 | 126 |  | Classrooms | k-6 | 33 | 25 | 825 | 33 | 0
5 | 112 | 124 | 107 | 128 | 126 | 133 | 141 | 124 | 130 | 161 |  |  | 7-12 | 35 | 27 | 945 | 35 | 0
6 | 114 | 100 | 117 | 116 | 119 | 130 | 125 | 124 | 153 | 140 |  |  | SPED | 5 | 15 | 75 | 5 | 0
7 | 108 | 103 | 107 | 119 | 117 | 77 | 1: 0; 2: 0; 3: 0; 4: 0; 10: 1845
8 | 100 | 108 | 114 | 117 | 102 | 0 | 1: 0; 2: 0; 3: 0; 4: 0
9 | 111 | 90 | 99 | 111 | 115 | 136 | 1: 117; 2: 119; 3: 142; 4: 149
10 | 92 | 120 | 102 | 125 | 136 | 99 | 1: 112; 2: 139; 3: 129; 4: 117
11 | 110 | 101 | 114 | 133 | 96 | 127 | 1: 136; 2: 121; 3: 116; 4: 119
12 | 99 | 104 | 130 | 98 | 96 | 13 | 1: 89; 2: 102; 3: 96; 4: 99
| 1520 | 1549 | 1590 | 1571 | 1527 | 1369 | 1: 1311; 2: 1319; 3: 1391; 4: 1391; 7: 24
| 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
| 1391 | 1391 | 1319 | 1311 | 1369 | 1527 | 1571 | 1590 | 1549 | 1520 | 1544 | 1568 | 1592 | 1616 | 1640
| 495228 | 493699 | 495689 | 496702 | 496918 | 497916 | 498003 | 499850 | 503096 | 503848 | 504600 | 505352 | 506104 | 506856 | 507608
1921

## PM Program
Sample Preventive Maintenance Program
System | Frequency | Qty | Unit | Cost per Unit | Sub Total | Misc Repairs (20%) | Soft Costs (15%) | Total Estimated Annual Amount
Roofing | Annual | 234387 | SF | 0.2 | 46877.4 | 9375.48 | 8437.932 | 64690.812 | 0.35911
HVAC | Annual | 153 | EA | 235 | 35955 | 7191 | 6471.9 | 49617.9 | 0.27544 | 6885 | 0.03822
Electrical Distribution | 3 Years | 79 | EA | 160 | 12640 | 2528 | 2275.2 | 17443.2 | 0.096831
Paving | 5 Years | 415133 | SF | 0.1 | 41513.3 | 8302.66 | 7472.394 | 57288.354 | 0.31802 | 0.030532
Plumbing | Annual | 8 | LS | 2500 | 20000 | 4000 | 3600 | 27600 | 0.15321
Total | [7 empty] | 216640.266 | 1.2026
180140
[8 empty] | 1.2026 | Per sqft
Less Paving = $0.83

## Financials
| 2nd Interim | Annual Revenue (Est)
Funding Source: | Ending Balance 2015/16 | 2016/17 |  | 2017/18 |  | 2018/19 |  | 2015/18 |  | 2016/19 |  | 2015/19 |  | 2016/20 |  | 2015/20 |  | 2016/21
|  | Revenue | Ending Bal | Revenue | Ending Bal | Revenue | Ending Bal | Revenue | Ending Bal | Revenue | Ending Bal | Revenue | Ending Bal | Revenue | Ending Bal | Revenue | Ending Bal | Revenue | Ending Bal
Fund 14 - Deferred Maintenance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fund 21 - Building (Capital Outlay)* | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fund 25 - Developer Fees** | 305708 | 0 | 305708 | 0 | 305708 | 0 | 305708 | 0 | 305708 | 0 | 305708 | 0 | 305708 | 0 | 305708 | 0 | 305708 | 0 | 305708
Fund 35 - County School Facilities Fund | 76
Prop 39 (Estimated) | 550000 | 0 | 550000 | 0 | 550000 | 0 | 550000 | 0 | 550000 | 0 | 550000 | 0 | 550000 | 0 | 550000 | 0 | 550000 | 0 | 550000
Cummulative Total | 855784 | 0 | 855708 | 0 | 855708 | 0 | 855708 | 0 | 855708 | 0 | 855708 | 0 | 855708 | 0 | 855708 | 0 | 855708 | 0 | 855708
*Assigned
**Committed
15/16 Budget
Expenditures | 21716080 | 0.1381% | 30402.512
3% RRMA | 651482.4
Building SF | 180140
CRV $350 per SF | 63049000
2% CRV | 1260980
Prop 39 | 550000

## MountainEmpireInventory
Current FY | 2019
[13 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
District | School | System | Building | Description | Identification | QTY (unit) | Cost Per Unit | Life Cycle | Is Portable | Installation Date | Condition | Cost to Replace* | Planned Replacement Date | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
Mountain Empire | MountainEmpireHS | Paving | Front Parking Lot | Asphalt Parking Lot | APL-FPL-18710 | 18710 | 7.5 | 30 | No | 1976 | 1 | 140325 | 2019 | 1 2019: 140325
Mountain Empire | MountainEmpireHS | Paving | Middle Parking Lot | Asphalt Parking Lot | APL-MPL-25922 | 25922 | 7.5 | 30 | No | 1976 | 1 | 194415 | 2019 | 1 2019: 194415
Mountain Empire | MountainEmpireHS | Paving | North Parking Lot | Asphalt Parking Lot | APL-NPL-44785 | 44785 | 7.5 | 30 | No | 2014 | 3 | 335887.5 | 2044
Mountain Empire | MountainEmpireHS | Paving | Fire Road | Asphalt Parking Lot | APL-FR-24262 | 24262 | 7.5 | 30 | No | 1976 | 1 | 181965 | 2019 | 1 2019: 181965
Mountain Empire | MountainEmpireHS | Paving | North Blacktop | Asphalt Playground | AP-NB-23103 | 23103 | 5.5 | 30 | No | 1976 | 1 | 127066.5 | 2019 | 1 2019: 127066.5
Mountain Empire | MountainEmpireHS | Paving | Maintenance Road | Asphalt Parking Lot | APL-MR-10332 | 10332 | 7.5 | 30 | No | 1976 | 1 | 77490 | 2019 | 1 2019: 77490
Mountain Empire | MountainEmpireHS | Paving | East Blacktop | Asphalt Playground | AP-EB-8890 | 8890 | 5.5 | 30 | No | 1976 | 1 | 48895 | 2019 | 1 2019: 48895
Mountain Empire | MountainEmpireHS | Paving | Handball Court | Asphalt Playground | AP-HC-3207 | 3207 | 5.5 | 30 | No | 1976 | 1 | 17638.5 | 2019 | 1 2019: 17638.5
Mountain Empire | MountainEmpireHS | Paving | Basketball Court | Asphalt Playground | AP-BC-14726 | 14726 | 5.5 | 30 | No | 1976 | 1 | 80993 | 2019 | 1 2019: 80993
Mountain Empire | MountainEmpireHS | Paving | District Office Parking Lot | Asphalt Parking Lot | APL-DOPL- | 1 | 7.5 | 30 | No | 1976 | 1 | 7.5 | 2019 | 1 2019: 7.5
Mountain Empire | MountainEmpireHS | Paving | MOT Parking | Asphalt Parking Lot | APL-MOTP- | 1 | 7.5 | 30 | No | 1976 | 1 | 7.5 | 2019 | 1 2019: 7.5
Mountain Empire | MountainEmpireHS | Paving | Front Parking Lot | Seal Coat and Stripe | SCS-FPL-18710 | 18710 | 0.35 | 5 | No | 1976 | 1 | 6548.5 | 2019 | 1 2019: 6548.5; 6 2024: 7530.775; 11 2029: 8513.05; 16 2034: 9495.325
Mountain Empire | MountainEmpireHS | Paving | Middle Parking Lot | Seal Coat and Stripe | SCS-MPL-25922 | 25922 | 0.35 | 5 | No | 1976 | 1 | 9072.7 | 2019 | 1 2019: 9072.7; 6 2024: 10433.605; 11 2029: 11794.51; 16 2034: 13155.415
Mountain Empire | MountainEmpireHS | Paving | North Parking Lot | Seal Coat and Stripe | SCS-NPL-44785 | 44785 | 0.35 | 5 | No | 2014 | 3 | 15674.75 | 2019 | 1 2019: 15674.75; 6 2024: 18025.9625; 11 2029: 20377.175; 16 2034: 22728.3875
Mountain Empire | MountainEmpireHS | Paving | Fire Road | Seal Coat and Stripe | SCS-FR-24262 | 24262 | 0.35 | 5 | No | 1976 | 1 | 8491.7 | 2019 | 1 2019: 8491.7; 6 2024: 9765.455; 11 2029: 11039.21; 16 2034: 12312.965
Mountain Empire | MountainEmpireHS | Paving | North Blacktop | Seal Coat and Stripe | SCS-NB-23103 | 23103 | 0.35 | 5 | No | 2014 | 3 | 8086.05 | 2019 | 1 2019: 8086.05; 6 2024: 9298.9575; 11 2029: 10511.865; 16 2034: 11724.7725
Mountain Empire | MountainEmpireHS | Paving | Maintenance Road | Seal Coat and Stripe | SCS-MR-10332 | 10332 | 0.35 | 5 | No | 1976 | 1 | 3616.2 | 2019 | 1 2019: 3616.2; 6 2024: 4158.63; 11 2029: 4701.06; 16 2034: 5243.49
Mountain Empire | MountainEmpireHS | Paving | East Blacktop | Seal Coat and Stripe | SCS-EB-8890 | 8890 | 0.35 | 5 | No | 1976 | 1 | 3111.5 | 2019 | 1 2019: 3111.5; 6 2024: 3578.225; 11 2029: 4044.95; 16 2034: 4511.675
Mountain Empire | MountainEmpireHS | Paving | Handball Court | Seal Coat and Stripe | SCS-HC-3207 | 3207 | 0.35 | 5 | No | 1976 | 1 | 1122.45 | 2019 | 1 2019: 1122.45; 6 2024: 1290.8175; 11 2029: 1459.185; 16 2034: 1627.5525
Mountain Empire | MountainEmpireHS | Paving | Basketball Court | Seal Coat and Stripe | SCS-BC-14726 | 14726 | 0.35 | 5 | No | 1976 | 1 | 5154.1 | 2019 | 1 2019: 5154.1; 6 2024: 5927.215; 11 2029: 6700.33; 16 2034: 7473.445
Mountain Empire | MountainEmpireHS | Paving | District Office Parking Lot | Seal Coat and Stripe | SCS-DOPL- | 1 | 0.35 | 5 | No | 1976 | 1 | 0.35 | 2019 | 1 2019: 0.35; 6 2024: 0.4025; 11 2029: 0.455; 16 2034: 0.5075
Mountain Empire | MountainEmpireHS | Paving | MOT Parking | Seal Coat and Stripe | SCS-MOTP- | 1 | 0.35 | 5 | No | 1976 | 1 | 0.35 | 2019 | 1 2019: 0.35; 6 2024: 0.4025; 11 2029: 0.455; 16 2034: 0.5075
Mountain Empire | MountainEmpireHS | Roofing | S | BUR - Gravel | Building S8 | 5519 | 18 | 30 | No | 1976 | 1 | 99342 | 2019 | 1 2019: 99342
Mountain Empire | MountainEmpireHS | Roofing | S | BUR - Gravel | Building S6 | 3247 | 18 | 30 | No | 1976 | 1 | 58446 | 2019 | 1 2019: 58446
Mountain Empire | MountainEmpireHS | Roofing | S | BUR - Gravel | Building S7 | 3834 | 18 | 30 | No | 1976 | 1 | 69012 | 2019 | 1 2019: 69012
Mountain Empire | MountainEmpireHS | HVAC | Admin | Package Unit 4 Ton | PUT-A-AC1 | 1 | 10000 | 15 | No | 2012 | 3 | 10000 | 2027 | 9 2027: 12400
Mountain Empire | MountainEmpireHS | HVAC | Admin | Package Unit 4 Ton | PUT-A-AC2 | 1 | 10000 | 15 | No | 2012 | 3 | 10000 | 2027 | 9 2027: 12400
Mountain Empire | MountainEmpireHS | HVAC | Admin | Package Unit 3.5 Ton | PUT-A-AC3 | 1 | 8750 | 15 | No | 2012 | 3 | 8750 | 2027 | 9 2027: 10850
Mountain Empire | MountainEmpireHS | HVAC | Admin | Package Unit 3.5 Ton | PUT-A-AC4 | 1 | 8750 | 15 | No | 2012 | 3 | 8750 | 2027 | 9 2027: 10850
Mountain Empire | MountainEmpireHS | HVAC | Admin | Package Unit 3.5 Ton | PUT-A-AC5 | 1 | 8750 | 15 | No | 2012 | 3 | 8750 | 2027 | 9 2027: 10850
Mountain Empire | MountainEmpireHS | HVAC | Admin | Package Unit 3.5 Ton | PUT-A-AC6 | 1 | 8750 | 15 | No | 2012 | 3 | 8750 | 2027 | 9 2027: 10850
Mountain Empire | MountainEmpireHS | HVAC | Admin | Package Unit 3.5 Ton | PUT-A-AC7 | 1 | 8750 | 15 | No | 2012 | 3 | 8750 | 2027 | 9 2027: 10850
Mountain Empire | MountainEmpireHS | HVAC | Admin | Package Unit 3.5 Ton | PUT-A-AC8 | 1 | 8750 | 15 | No | 2005 | 3 | 8750 | 2020 | 2 2020: 9012.5; 17 2035: 12950
Mountain Empire | MountainEmpireHS | HVAC | Admin | Package Unit 4 Ton | PUT-A-AC9 | 1 | 10000 | 15 | No | 2012 | 3 | 10000 | 2027 | 9 2027: 12400
Mountain Empire | MountainEmpireHS | HVAC | Admin | Package Unit 4 Ton | PUT-A-AC10 | 1 | 10000 | 15 | No | 2012 | 3 | 10000 | 2027 | 9 2027: 12400
Mountain Empire | MountainEmpireHS | HVAC | Admin | Package Unit 5 Ton | PUT-A-AC11 | 1 | 12500 | 15 | No | 2012 | 3 | 12500 | 2027 | 9 2027: 15500
Mountain Empire | MountainEmpireHS | Finishes | Admin | Carpet Tile |  | 8895 | 8.25 | 10 | No | 2015 | 1 | 73383.75 | 2019 | 1 2019: 73383.75; 11 2029: 95398.875
Mountain Empire | MountainEmpireHS | Finishes | S | Carpet Roll |  | 25359 | 7.9 | 15 | No | 1990 | 2 | 200336.1 | 2019 | 1 2019: 200336.1; 16 2034: 290487.345
Mountain Empire | MountainEmpireHS | Finishes | Gym | Carpet Roll |  | 24579 | 7.9 | 15 | No | 2014 | 2 | 194174.1 | 2026 | 8 2026: 234950.661
Mountain Empire | MountainEmpireHS | Finishes | Mirror Room | Carpet Roll |  | 2652 | 7.9 | 15 | No | 2014 | 2 | 20950.8 | 2026 | 8 2026: 25350.468
Mountain Empire | MountainEmpireHS | Plumbing | Admin | Water Heater 10 Gallon Electric |  | 1 | 1250 | 10 | No | 1985 | 3 | 1250 | 2019 | 1 2019: 1250; 11 2029: 1625
Mountain Empire | MountainEmpireHS | Electrical | Admin | Panel 100A 208/120 3P | Admin-Panel A | 1 | 8500 | 30 | No | 1985 | 3 | 8500 | 2019 | 1 2019: 8500
Mountain Empire | MountainEmpireHS | Electrical | Admin | Panel 100A 208/120 3P | Admin-Panel B | 1 | 8500 | 30 | No | 1985 | 3 | 8500 | 2019 | 1 2019: 8500
Mountain Empire | MountainEmpireHS | Electrical | Admin | Panel 100A 208/120 3P | Admin-Panel D | 1 | 8500 | 30 | No | 1985 | 3 | 8500 | 2019 | 1 2019: 8500
Mountain Empire | MountainEmpireHS | Electrical | Admin | Panel 400A 208/120 3P | Admin-Panel C | 1 | 13500 | 30 | No | 1985 | 3 | 13500 | 2019 | 1 2019: 13500
Mountain Empire | MountainEmpireHS | Plumbing | Admin | DCW/Sewer |  | 11395 | 18 | 30 | No | 1985 | 2 | 205110 | 2019 | 1 2019: 205110
Mountain Empire | MountainEmpireHS | LowVoltage | Admin | FACP |  | 1 | 20000 | 15 | No | 2000 | 3 | 20000 | 2019 | 1 2019: 20000; 16 2034: 29000
Mountain Empire | MountainEmpireHS | LowVoltage | Admin | Clock/Bell/Paging |  | 1 | 40000 | 20 | No | 2000 | 3 | 40000 | 2020 | 2 2020: 41200
Mountain Empire | MountainEmpireHS | Roofing | S | BUR - Gravel | Building S9 | 2442 | 18 | 30 | No | 1976 | 1 | 43956 | 2019 | 1 2019: 43956
Mountain Empire | MountainEmpireHS | Roofing | S | Ashpalt Shingle | Building S1 | 2670 | 9.5 | 15 | No | 2004 | 1 | 25365 | 2019 | 1 2019: 25365; 16 2034: 36779.25
Mountain Empire | MountainEmpireHS | Roofing | S | Ashpalt Shingle | Building S2 | 2833 | 9.5 | 15 | No | 1976 | 1 | 26913.5 | 2019 | 1 2019: 26913.5; 16 2034: 39024.575
Mountain Empire | MountainEmpireHS | Roofing | S | Ashpalt Shingle | Building S3 | 3394 | 9.5 | 15 | No | 1976 | 1 | 32243 | 2019 | 1 2019: 32243; 16 2034: 46752.35
Mountain Empire | MountainEmpireHS | Roofing | Gym | BUR - Gravel | Building L6 | 2689 | 18 | 30 | No | 1976 | 1 | 48402 | 2019 | 1 2019: 48402
Mountain Empire | MountainEmpireHS | Roofing | L3 | Ashpalt Shingle | Builidng L3 | 2184 | 9.5 | 15 | No | 1976 | 1 | 20748 | 2019 | 1 2019: 20748; 16 2034: 30084.6
Mountain Empire | MountainEmpireHS | Roofing | S | BUR - Gravel | Building S Breezeway | 951 | 18 | 30 | No | 1976 | 1 | 17118 | 2019 | 1 2019: 17118
Mountain Empire | MountainEmpireHS | Roofing | S | Ashpalt Shingle | Building S4 | 1942 | 9.5 | 15 | No | 1976 | 2 | 18449 | 2019 | 1 2019: 18449; 16 2034: 26751.05
Mountain Empire | MountainEmpireHS | Roofing | S | Ashpalt Shingle | Building S5 | 1751 | 9.5 | 15 | No | 2004 | 2 | 16634.5 | 2019 | 1 2019: 16634.5; 16 2034: 24120.025
Mountain Empire | MountainEmpireHS | Roofing | P2 | Standing Seam | Building P2 | 1117 | 25 | 25 | Yes | 1988 | 2 | 27925 | 2019 | 1 2019: 27925
Mountain Empire | MountainEmpireHS | Roofing | P4 | Standing Seam | Building P4 | 1157 | 25 | 25 | Yes | 1988 | 2 | 28925 | 2019 | 1 2019: 28925
Mountain Empire | MountainEmpireHS | Roofing | P6 | Standing Seam | Building P6 | 1090 | 25 | 25 | Yes | 1993 | 2 | 27250 | 2019 | 1 2019: 27250
Mountain Empire | MountainEmpireHS | Roofing | P7 | Standing Seam | Building P7 | 1119 | 25 | 25 | Yes | 1993 | 2 | 27975 | 2019 | 1 2019: 27975
Mountain Empire | MountainEmpireHS | Roofing | P8 | Standing Seam | Building P8 | 1110 | 25 | 25 | Yes | 1993 | 2 | 27750 | 2019 | 1 2019: 27750
Mountain Empire | MountainEmpireHS | Roofing | P9 | BUR - Gran Cap | Building P9 | 1242 | 15 | 25 | Yes | 1993 | 2 | 18630 | 2019 | 1 2019: 18630
Mountain Empire | MountainEmpireHS | Roofing | P3 | BUR - Gran Cap | Building P3 | 1073 | 15 | 25 | Yes | 1995 | 2 | 16095 | 2019 | 1 2019: 16095
Mountain Empire | MountainEmpireHS | Roofing | P1 | Standing Seam | Building P1 | 2095 | 25 | 25 | Yes | 2001 | 2 | 52375 | 2021 | 3 2021: 55517.5
Mountain Empire | MountainEmpireHS | Roofing | P5 | Standing Seam | Building P5 | 1142 | 25 | 25 | Yes | 2001 | 2 | 28550 | 2021 | 3 2021: 30263
Mountain Empire | MountainEmpireHS | Roofing | Kitchen | BUR - Gravel | Kitchen | 429 | 18 | 30 | No | 1976 | 3 | 7722 | 2019 | 1 2019: 7722
Mountain Empire | MountainEmpireHS | Roofing | Gym | Ashpalt Shingle | Builidng L5 | 2511 | 9.5 | 15 | No | 2015 | 3 | 23854.5 | 2030 | 12 2030: 31726.485
Mountain Empire | MountainEmpireHS | Roofing | Gym | BUR - Gran Cap | Building L7 | 11479 | 15 | 25 | No | 1976 | 3 | 172185 | 2019 | 1 2019: 172185
Mountain Empire | MountainEmpireHS | Roofing | L1 | Ashpalt Shingle | Building L1 | 1336 | 9.5 | 15 | No | 1976 | 3 | 12692 | 2019 | 1 2019: 12692; 16 2034: 18403.4
Mountain Empire | MountainEmpireHS | Roofing | L1 | BUR - Gravel | Building L Breezeway | 2289 | 18 | 30 | No | 1976 | 3 | 41202 | 2019 | 1 2019: 41202
Mountain Empire | MountainEmpireHS | Roofing | L4 | Ashpalt Shingle | Building L4 | 1789 | 9.5 | 15 | No | 1976 | 3 | 16995.5 | 2019 | 1 2019: 16995.5; 16 2034: 24643.475
Mountain Empire | MountainEmpireHS | Roofing | Mirror Room | SP - TPO | Mirror Room | 2652 | 12 | 10 | No | 2015 | 3 | 31824 | 2025 | 7 2025: 37552.32; 17 2035: 47099.52
Mountain Empire | MountainEmpireHS | Roofing | Admin | BUR - Gravel | BURG-AdminP-A | 11701 | 18 | 30 | No | 1985 | 3 | 210618 | 2019 | 1 2019: 210618
Mountain Empire | MountainEmpireHS | Roofing | Admin | Ashpalt Shingle | AS-AdminP-A2 | 1704 | 9.5 | 15 | No | 2005 | 3 | 16188 | 2020 | 2 2020: 16673.64; 17 2035: 23958.24
Mountain Empire | MountainEmpireHS | Roofing | Admin | Ashpalt Shingle | AS-AdminP-A3 | 1547 | 9.5 | 15 | No | 1985 | 3 | 14696.5 | 2019 | 1 2019: 14696.5; 16 2034: 21309.925
Mountain Empire | MountainEmpireHS | Roofing | P10 | BUR - Gran Cap | Building P10 | 599 | 15 | 25 | Yes | 1985 | 3 | 8985 | 2019 | 1 2019: 8985
Mountain Empire | MountainEmpireHS | Roofing | Q1 | SP - TPO | Building Q1 | 1518 | 12 | 10 | No | 2015 | 3 | 18216 | 2025 | 7 2025: 21494.88; 17 2035: 26959.68
Mountain Empire | MountainEmpireHS | HVAC | S | Package Unit 25 Ton | PUT-S-AC1 | 1 | 62500 | 20 | No | 2013 | 3 | 62500 | 2033 | 15 2033: 88750
Mountain Empire | MountainEmpireHS | HVAC | S | Package Unit 20 Ton | PUT-S-AC2 | 1 | 50000 | 20 | No | 2013 | 3 | 50000 | 2033 | 15 2033: 71000
Mountain Empire | MountainEmpireHS | HVAC | S | Package Unit 25 Ton | PUT-S-AC3 | 1 | 62500 | 20 | No | 2013 | 3 | 62500 | 2033 | 15 2033: 88750
Mountain Empire | MountainEmpireHS | HVAC | S | Package Unit 3 Ton | PUT-S-AC4 | 1 | 7500 | 15 | No | 1990 | 3 | 7500 | 2019 | 1 2019: 7500; 16 2034: 10875
Mountain Empire | MountainEmpireHS | HVAC | S | Package Unit 3 Ton | PUT-S-AC5 | 1 | 7500 | 15 | No | 1990 | 3 | 7500 | 2019 | 1 2019: 7500; 16 2034: 10875
Mountain Empire | MountainEmpireHS | HVAC | L1 | Package Unit 20 Ton | PUT-L1-AC1 | 1 | 50000 | 20 | No | 1994 | 3 | 50000 | 2019 | 1 2019: 50000
Mountain Empire | MountainEmpireHS | HVAC | L1 | Package Unit 10 Ton | PUT-L1-AC2 | 1 | 25000 | 15 | No | 1990 | 3 | 25000 | 2019 | 1 2019: 25000; 16 2034: 36250
Mountain Empire | MountainEmpireHS | HVAC | L1 | Package Unit 10 Ton | PUT-L1-AC3 | 1 | 25000 | 15 | No | 1990 | 3 | 25000 | 2019 | 1 2019: 25000; 16 2034: 36250
Mountain Empire | MountainEmpireHS | HVAC | L1 | Package Unit 2.5 Ton | PUT-L1-AC4 | 1 | 6250 | 15 | No | 1990 | 3 | 6250 | 2019 | 1 2019: 6250; 16 2034: 9062.5
Mountain Empire | MountainEmpireHS | HVAC | L1 | Heater/Ventilation 100K BTU | PUT-L1-AC5 | 1 | 10000 | 15 | No | 1995 | 3 | 10000 | 2019 | 1 2019: 10000; 16 2034: 14500
Mountain Empire | MountainEmpireHS | HVAC | L1 | Heater/Ventilation 250K BTU | PUT-L1-AC6 | 1 | 20000 | 15 | No | 1995 | 3 | 20000 | 2019 | 1 2019: 20000; 16 2034: 29000
Mountain Empire | MountainEmpireHS | HVAC | L1 | Heater/Ventilation 250K BTU | PUT-L1-AC7 | 1 | 20000 | 15 | No | 1995 | 3 | 20000 | 2019 | 1 2019: 20000; 16 2034: 29000
Mountain Empire | MountainEmpireHS | HVAC | Mirror Room | Package Unit 4 Ton | PUT-MR-1 | 1 | 10000 | 15 | No | 2000 | 3 | 10000 | 2019 | 1 2019: 10000; 16 2034: 14500
Mountain Empire | MountainEmpireHS | HVAC | Q1 | Package Unit 4 Ton | PUT-Q-1 | 1 | 10000 | 15 | No | 1991 | 3 | 10000 | 2019 | 1 2019: 10000; 16 2034: 14500
Mountain Empire | MountainEmpireHS | HVAC | Kitchen | Heat Pump | HP-K-1 | 1 | 12000 | 15 | Yes | 2000 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P1 | Heat Pump | HP-P1-1 | 1 | 12000 | 15 | Yes | 2001 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P1 | Heat Pump | HP-P1-2 | 1 | 12000 | 15 | Yes | 2001 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P2 | Heat Pump | HP-P2-1 | 1 | 12000 | 15 | Yes | 1988 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P5 | Heat Pump | HP-P5-1 | 1 | 12000 | 15 | Yes | 2001 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P4 | Heat Pump | HP-P4-1 | 1 | 12000 | 15 | Yes | 1988 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P3 | Heat Pump | HP-P3-1 | 1 | 12000 | 15 | Yes | 1995 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P3 | Heat Pump | HP-P3-2 | 1 | 12000 | 15 | Yes | 1995 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P6 | Heat Pump | HP-P6-1 | 1 | 12000 | 15 | Yes | 1993 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P7 | Heat Pump | HP-P7-1 | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | MountainEmpireHS | HVAC | P8 | Heat Pump | HP-P8-1 | 1 | 12000 | 15 | Yes | 1993 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P9 | Heat Pump | HP-P9-1 | 1 | 12000 | 15 | Yes | 1993 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P9 | Heat Pump | HP-P9-2 | 1 | 12000 | 15 | Yes | 1993 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | HVAC | P10 | Heat Pump | HP-P10-1 | 1 | 12000 | 15 | Yes | 2000 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireHS | Finishes | Q1 | Carpet Roll |  | 1518 | 7.9 | 15 | Yes | 1991 | 2 | 11992.2 | 2019 | 1 2019: 11992.2; 16 2034: 17388.69
Mountain Empire | MountainEmpireHS | Finishes | P1 | Carpet Roll |  | 2095 | 7.9 | 15 | Yes | 2001 | 2 | 16550.5 | 2019 | 1 2019: 16550.5; 16 2034: 23998.225
Mountain Empire | MountainEmpireHS | Finishes | P2 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1988 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | MountainEmpireHS | Finishes | P3 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1995 | 1 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | MountainEmpireHS | Finishes | P4 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1988 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | MountainEmpireHS | Finishes | P5 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2001 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | MountainEmpireHS | Finishes | P6 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1993 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | MountainEmpireHS | Finishes | P7 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1993 | 1 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | MountainEmpireHS | Finishes | P8 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1993 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | MountainEmpireHS | Finishes | P9 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1993 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | MountainEmpireHS | Finishes | P10 | Carpet Roll |  | 600 | 7.9 | 15 | Yes | 2000 | 2 | 4740 | 2019 | 1 2019: 4740; 16 2034: 6873
Mountain Empire | MountainEmpireHS | Finishes | Admin | Custom Exterior |  | 11395 | 6.5 | 20 | No | 2000 | 1 | 74067.5 | 2019 | 1 2019: 74067.5
Mountain Empire | MountainEmpireHS | Finishes | S | Custom Exterior |  | 25359 | 6.5 | 20 | No | 2000 | 1 | 164833.5 | 2019 | 1 2019: 164833.5
Mountain Empire | MountainEmpireHS | Finishes | Gym | Custom Exterior |  | 24579 | 6.5 | 20 | No | 2000 | 1 | 159763.5 | 2019 | 1 2019: 159763.5
Mountain Empire | MountainEmpireHS | Finishes | Mirror Room | Custom Exterior |  | 2652 | 6.5 | 20 | No | 2000 | 1 | 17238 | 2019 | 1 2019: 17238
Mountain Empire | MountainEmpireHS | Finishes | Gym | Paint Exterior |  | 24579 | 1.6 | 10 | No | 2000 | 1 | 39326.4 | 2019 | 1 2019: 39326.4; 11 2029: 51124.32
Mountain Empire | MountainEmpireHS | Finishes | Mirror Room | Paint Exterior |  | 2652 | 1.6 | 10 | No | 2000 | 3 | 4243.2 | 2019 | 1 2019: 4243.2; 11 2029: 5516.16
Mountain Empire | MountainEmpireHS | Finishes | Q1 | Paint Exterior |  | 1518 | 1.6 | 10 | Yes | 1991 | 3 | 2428.8 | 2019 | 1 2019: 2428.8; 11 2029: 3157.44
Mountain Empire | MountainEmpireHS | Finishes | P1 | Paint Exterior |  | 2095 | 1.6 | 10 | Yes | 2001 | 3 | 3352 | 2019 | 1 2019: 3352; 11 2029: 4357.6
Mountain Empire | MountainEmpireHS | Finishes | P2 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1988 | 1 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | MountainEmpireHS | Finishes | P3 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1995 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | MountainEmpireHS | Finishes | P4 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1988 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | MountainEmpireHS | Finishes | P5 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2001 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | MountainEmpireHS | Finishes | P6 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1993 | 1 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | MountainEmpireHS | Finishes | P7 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1993 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | MountainEmpireHS | Finishes | P8 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1993 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | MountainEmpireHS | Finishes | P9 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1993 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | MountainEmpireHS | Finishes | P10 | Paint Exterior |  | 600 | 1.6 | 10 | Yes | 2000 | 1 | 960 | 2019 | 1 2019: 960; 11 2029: 1248
Mountain Empire | MountainEmpireHS | Finishes | Admin | Paint Interior |  | 11395 | 1.5 | 10 | No | 2000 | 2 | 17092.5 | 2019 | 1 2019: 17092.5; 11 2029: 22220.25
Mountain Empire | MountainEmpireHS | Finishes | S | Paint Interior |  | 25359 | 1.5 | 10 | No | 2000 | 1 | 38038.5 | 2019 | 1 2019: 38038.5; 11 2029: 49450.05
Mountain Empire | MountainEmpireHS | Finishes | Gym | Paint Interior |  | 24579 | 1.5 | 10 | No | 2000 | 1 | 36868.5 | 2019 | 1 2019: 36868.5; 11 2029: 47929.05
Mountain Empire | MountainEmpireHS | Finishes | Mirror Room | Paint Interior |  | 2652 | 1.5 | 10 | No | 2000 | 1 | 3978 | 2019 | 1 2019: 3978; 11 2029: 5171.4
Mountain Empire | MountainEmpireHS | Finishes | Q1 | Paint Interior |  | 1518 | 1.5 | 10 | Yes | 1991 | 2 | 2277 | 2019 | 1 2019: 2277; 11 2029: 2960.1
Mountain Empire | MountainEmpireHS | Finishes | P1 | Paint Interior |  | 2095 | 1.5 | 10 | Yes | 2001 | 2 | 3142.5 | 2019 | 1 2019: 3142.5; 11 2029: 4085.25
Mountain Empire | MountainEmpireHS | Finishes | P2 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1988 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | MountainEmpireHS | Finishes | P3 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1995 | 1 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | MountainEmpireHS | Finishes | P4 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1988 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | MountainEmpireHS | Finishes | P5 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2001 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | MountainEmpireHS | Finishes | P6 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1993 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | MountainEmpireHS | Finishes | P7 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1993 | 1 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | MountainEmpireHS | Finishes | P8 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1993 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | MountainEmpireHS | Finishes | P9 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1993 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | MountainEmpireHS | Finishes | P10 | Paint Interior |  | 600 | 1.5 | 10 | Yes | 2000 | 2 | 900 | 2019 | 1 2019: 900; 11 2029: 1170
Mountain Empire | MountainEmpireHS | Finishes | Admin | Vinyl Tile |  | 2500 | 6.5 | 12 | No | 2000 | 1 | 16250 | 2019 | 1 2019: 16250; 13 2031: 22100
Mountain Empire | MountainEmpireHS | Plumbing | S | DCW/Sewer |  | 25359 | 18 | 30 | No | 1976 | 3 | 456462 | 2019 | 1 2019: 456462
Mountain Empire | MountainEmpireHS | Plumbing | Gym | DCW/Sewer |  | 24579 | 18 | 30 | No | 1976 | 2 | 442422 | 2019 | 1 2019: 442422
Mountain Empire | MountainEmpireHS | Plumbing | Mirror Room | DCW/Sewer |  | 2652 | 18 | 30 | No | 1984 | 3 | 47736 | 2019 | 1 2019: 47736
Mountain Empire | MountainEmpireHS | Plumbing | Q1 | DCW/Sewer |  | 1518 | 18 | 30 | Yes | 1991 | 3 | 27324 | 2021 | 3 2021: 28963.44
Mountain Empire | MountainEmpireHS | Plumbing | P1 | DCW/Sewer |  | 2095 | 18 | 30 | Yes | 2001 | 3 | 37710 | 2031 | 13 2031: 51285.6
Mountain Empire | MountainEmpireHS | Plumbing | P2 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1988 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | MountainEmpireHS | Plumbing | P3 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1995 | 3 | 17280 | 2025 | 7 2025: 20390.4
Mountain Empire | MountainEmpireHS | Plumbing | P4 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1988 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | MountainEmpireHS | Plumbing | P5 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2001 | 3 | 17280 | 2031 | 13 2031: 23500.8
Mountain Empire | MountainEmpireHS | Plumbing | P6 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1993 | 3 | 17280 | 2023 | 5 2023: 19353.6
Mountain Empire | MountainEmpireHS | Plumbing | P7 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1993 | 3 | 17280 | 2023 | 5 2023: 19353.6
Mountain Empire | MountainEmpireHS | Plumbing | P8 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1993 | 3 | 17280 | 2023 | 5 2023: 19353.6
Mountain Empire | MountainEmpireHS | Plumbing | P9 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1993 | 3 | 17280 | 2023 | 5 2023: 19353.6
Mountain Empire | MountainEmpireHS | Plumbing | P10 | DCW/Sewer |  | 600 | 18 | 30 | Yes | 1985 | 3 | 10800 | 2019 | 1 2019: 10800
Mountain Empire | MountainEmpireHS | Fencing |  | 2" Chain Link, Galv, 6' |  | 5497 | 22.5 | 15 | No | 1980 | 3 | 123682.5 | 2019 | 1 2019: 123682.5; 16 2034: 179339.625
Mountain Empire | MountainEmpireHS | Electrical | Admin | Fluorescent CR Lighting |  | 11395 | 4 | 20 | No | 2000 | 3 | 45580 | 2020 | 2 2020: 46947.4
Mountain Empire | MountainEmpireHS | Electrical | S | Fluorescent CR Lighting |  | 25359 | 4 | 20 | No | 2000 | 3 | 101436 | 2020 | 2 2020: 104479.08
Mountain Empire | MountainEmpireHS | Electrical | Gym | Fluorescent CR Lighting |  | 24579 | 4 | 20 | No | 2000 | 3 | 98316 | 2020 | 2 2020: 101265.48
Mountain Empire | MountainEmpireHS | Electrical | Mirror Room | Fluorescent CR Lighting |  | 2652 | 4 | 20 | No | 2000 | 3 | 10608 | 2020 | 2 2020: 10926.24
Mountain Empire | MountainEmpireHS | Electrical | Q1 | Fluorescent CR Lighting |  | 1518 | 4 | 20 | Yes | 1991 | 3 | 6072 | 2019 | 1 2019: 6072
Mountain Empire | MountainEmpireHS | Electrical | P1 | Fluorescent CR Lighting |  | 2095 | 4 | 20 | Yes | 2001 | 3 | 8380 | 2021 | 3 2021: 8882.8
Mountain Empire | MountainEmpireHS | Electrical | P2 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1988 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | MountainEmpireHS | Electrical | P3 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1995 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | MountainEmpireHS | Electrical | P4 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1988 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | MountainEmpireHS | Electrical | P5 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2001 | 3 | 3840 | 2021 | 3 2021: 4070.4
Mountain Empire | MountainEmpireHS | Electrical | P6 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1993 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | MountainEmpireHS | Electrical | P7 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1993 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | MountainEmpireHS | Electrical | P8 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1993 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | MountainEmpireHS | Electrical | P9 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1993 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | MountainEmpireHS | Electrical | P10 | Fluorescent CR Lighting |  | 600 | 4 | 20 | Yes | 2000 | 3 | 2400 | 2020 | 2 2020: 2472
Mountain Empire | Campo | Paving | Parking Lot | Asphalt Parking Lot |  | 22008 | 7.5 | 30 | No | 1990 | 1 | 165060 | 2019 | 1 2019: 165060
Mountain Empire | Campo | Paving | Blacktop | Asphalt Playground |  | 28048 | 5.5 | 30 | No | 2015 | 3 | 154264 | 2045
Mountain Empire | Campo | Paving | Drop Off Loop | Asphalt Parking Lot |  | 38734 | 7.5 | 30 | No | 1990 | 1 | 290505 | 2019 | 1 2019: 290505
Mountain Empire | Campo | Paving | Parking Lot | Seal Coat and Stripe |  | 22008 | 0.35 | 5 | No | 2015 | 3 | 7702.8 | 2020 | 2 2020: 7933.884; 7 2025: 9089.304; 12 2030: 10244.724; 17 2035: 11400.144
Mountain Empire | Campo | Paving | Blacktop | Seal Coat and Stripe |  | 28048 | 0.35 | 5 | No | 2015 | 3 | 9816.8 | 2020 | 2 2020: 10111.304; 7 2025: 11583.824; 12 2030: 13056.344; 17 2035: 14528.864
Mountain Empire | Campo | Paving | Drop Off Loop | Seal Coat and Stripe |  | 38734 | 0.35 | 5 | No | 2015 | 3 | 13556.9 | 2020 | 2 2020: 13963.607; 7 2025: 15997.142; 12 2030: 18030.677; 17 2035: 20064.212
Mountain Empire | Campo | Playground | Kinder Playground | Wood Fiber |  | 2860 | 3.15 | 5 | No | 1990 | 2 | 9009 | 2019 | 1 2019: 9009; 6 2024: 10360.35; 11 2029: 11711.7; 16 2034: 13063.05
Mountain Empire | Campo | Playground | Primary Playground | Wood Fiber |  | 3746 | 3.15 | 5 | No | 1990 | 2 | 11799.9 | 2019 | 1 2019: 11799.9; 6 2024: 13569.885; 11 2029: 15339.87; 16 2034: 17109.855
Mountain Empire | Campo | Playground | Swings | Wood Fiber |  | 3269 | 3.15 | 5 | No | 2003 | 2 | 10297.35 | 2019 | 1 2019: 10297.35; 6 2024: 11841.9525; 11 2029: 13386.555; 16 2034: 14931.1575
Mountain Empire | Campo | Fencing |  | 2" Chain Link, Galv, 6' | Perimeter Fence | 2597 | 22.5 | 15 | No | 1990 | 3 | 58432.5 | 2019 | 1 2019: 58432.5; 16 2034: 84727.125
Mountain Empire | Campo | Fencing |  | 2" Chain Link, Galv, 6' | Parking Lot Fence | 507 | 22.5 | 15 | No | 1990 | 3 | 11407.5 | 2019 | 1 2019: 11407.5; 16 2034: 16540.875
Mountain Empire | Campo | Fencing |  | 2" Chain Link, Galv, 6' | Well Fence | 274 | 22.5 | 15 | No | 1990 | 3 | 6165 | 2019 | 1 2019: 6165; 16 2034: 8939.25
Mountain Empire | Campo | Fencing |  | 2" Chain Link, Galv, 6' | Solar Fence | 533 | 22.5 | 15 | No | 2012 | 3 | 11992.5 | 2027 | 9 2027: 14870.7
Mountain Empire | Campo | Fencing |  | 16ga Iron Fence 6' | Iron Kinder Fence | 162 | 110 | 25 | No | 1990 | 1 | 17820 | 2019 | 1 2019: 17820
Mountain Empire | Campo | Roofing | Classroom Building | BUR - Gran Cap | Main Roof Section | 20484 | 15 | 25 | No | 1990 | 2 | 307260 | 2019 | 1 2019: 307260
Mountain Empire | Campo | Roofing | Classroom Building | BUR - Gran Cap | CR Building A | 332 | 15 | 25 | No | 1990 | 2 | 4980 | 2019 | 1 2019: 4980
Mountain Empire | Campo | Roofing | Classroom Building | BUR - Gran Cap | CR Building B | 184 | 15 | 25 | No | 1990 | 2 | 2760 | 2019 | 1 2019: 2760
Mountain Empire | Campo | Roofing | Classroom Building | BUR - Gran Cap | CR Building C | 172 | 15 | 25 | No | 1990 | 2 | 2580 | 2019 | 1 2019: 2580
Mountain Empire | Campo | Roofing | Classroom Building | BUR - Gran Cap | CR Building D | 308 | 15 | 25 | No | 1990 | 2 | 4620 | 2019 | 1 2019: 4620
Mountain Empire | Campo | Roofing | Classroom Building | BUR - Gran Cap | CR Building E | 494 | 15 | 25 | No | 1990 | 2 | 7410 | 2019 | 1 2019: 7410
Mountain Empire | Campo | Roofing | Classroom Building | BUR - Gran Cap | CR Building F | 516 | 15 | 25 | No | 1990 | 2 | 7740 | 2019 | 1 2019: 7740
Mountain Empire | Campo | Roofing | Classroom Building | BUR - Gran Cap | CR Brow A | 110 | 15 | 25 | No | 1990 | 2 | 1650 | 2019 | 1 2019: 1650
Mountain Empire | Campo | Roofing | Classroom Building | BUR - Gran Cap | CR Brow B | 128 | 15 | 25 | No | 1990 | 2 | 1920 | 2019 | 1 2019: 1920
Mountain Empire | Campo | Roofing | Classroom Building | BUR - Gran Cap | CR Building N | 78 | 15 | 25 | No | 1990 | 2 | 1170 | 2019 | 1 2019: 1170
Mountain Empire | Campo | Roofing | Classroom Building | Ashpalt Shingle | CR Building G | 560 | 9.5 | 15 | No | 1990 | 2 | 5320 | 2019 | 1 2019: 5320; 16 2034: 7714
Mountain Empire | Campo | Roofing | Classroom Building | Ashpalt Shingle | CR Building H | 548 | 9.5 | 15 | No | 1990 | 1 | 5206 | 2019 | 1 2019: 5206; 16 2034: 7548.7
Mountain Empire | Campo | Roofing | Classroom Building | Ashpalt Shingle | CR Building I | 886 | 9.5 | 15 | No | 1990 | 2 | 8417 | 2019 | 1 2019: 8417; 16 2034: 12204.65
Mountain Empire | Campo | Roofing | Classroom Building | Ashpalt Shingle | CR Building J | 303 | 9.5 | 15 | No | 1990 | 2 | 2878.5 | 2019 | 1 2019: 2878.5; 16 2034: 4173.825
Mountain Empire | Campo | Roofing | Classroom Building | Ashpalt Shingle | CR Building K | 292 | 9.5 | 15 | No | 1990 | 2 | 2774 | 2019 | 1 2019: 2774; 16 2034: 4022.3
Mountain Empire | Campo | Roofing | Classroom Building | Ashpalt Shingle | CR Building L | 69 | 9.5 | 15 | No | 1990 | 2 | 655.5 | 2019 | 1 2019: 655.5; 16 2034: 950.475
Mountain Empire | Campo | Roofing | Classroom Building | Ashpalt Shingle | CR Building M | 78 | 9.5 | 15 | No | 1990 | 2 | 741 | 2019 | 1 2019: 741; 16 2034: 1074.45
Mountain Empire | Campo | Roofing | Classroom Building | Ashpalt Shingle | CR Building O | 83 | 9.5 | 15 | No | 1990 | 2 | 788.5 | 2019 | 1 2019: 788.5; 16 2034: 1143.325
Mountain Empire | Campo | Roofing | South Wing | BUR - Gran Cap | South Wing | 7151 | 15 | 25 | No | 2004 | 3 | 107265 | 2029 | 11 2029: 139444.5
Mountain Empire | Campo | Roofing | South Wing | Ashpalt Shingle | SW A | 1181 | 9.5 | 15 | No | 2004 | 3 | 11219.5 | 2019 | 1 2019: 11219.5; 16 2034: 16268.275
Mountain Empire | Campo | Roofing | South Wing | Ashpalt Shingle | SW B | 256 | 9.5 | 15 | No | 2004 | 3 | 2432 | 2019 | 1 2019: 2432; 16 2034: 3526.4
Mountain Empire | Campo | Roofing | South Wing | Ashpalt Shingle | SW C | 614 | 9.5 | 15 | No | 2004 | 3 | 5833 | 2019 | 1 2019: 5833; 16 2034: 8457.85
Mountain Empire | Campo | Roofing | South Wing | Ashpalt Shingle | SW D | 54 | 9.5 | 15 | No | 2004 | 3 | 513 | 2019 | 1 2019: 513; 16 2034: 743.85
Mountain Empire | Campo | Roofing | P1 | BUR - Gran Cap | P1 | 1130 | 15 | 25 | Yes | 1992 | 3 | 16950 | 2019 | 1 2019: 16950
Mountain Empire | Campo | Roofing | P2 | Standing Seam | P2 | 1180 | 25 | 25 | Yes | 1992 | 3 | 29500 | 2019 | 1 2019: 29500
Mountain Empire | Campo | Roofing | P3 | Standing Seam | P3 | 1209 | 25 | 25 | Yes | 1992 | 3 | 30225 | 2019 | 1 2019: 30225
Mountain Empire | Campo | Roofing | P4 | Standing Seam | P4 | 1178 | 25 | 25 | Yes | 2006 | 3 | 29450 | 2031 | 13 2031: 40052
Mountain Empire | Campo | Roofing | P5 | Standing Seam | P5 | 1114 | 25 | 25 | Yes | 2006 | 3 | 27850 | 2031 | 13 2031: 37876
Mountain Empire | Campo | Roofing | Pump House | BUR - Gran Cap | Pump House | 348 | 15 | 25 | No | 1990 | 3 | 5220 | 2019 | 1 2019: 5220
Mountain Empire | Campo | Roofing | Shade Structure | Vinyl Fabric | Shade Structure | 260 | 15 | 10 | No | 2003 | 3 | 3900 | 2019 | 1 2019: 3900; 11 2029: 5070
Mountain Empire | Campo | Plumbing | Classroom Building | DCW/Sewer |  | 25287 | 18 | 30 | No | 1990 | 3 | 455166 | 2020 | 2 2020: 468820.98
Mountain Empire | Campo | Plumbing | P1 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1992 | 3 | 17280 | 2022 | 4 2022: 18835.2
Mountain Empire | Campo | Plumbing | P2 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1992 | 3 | 17280 | 2022 | 4 2022: 18835.2
Mountain Empire | Campo | Plumbing | P3 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1992 | 3 | 17280 | 2022 | 4 2022: 18835.2
Mountain Empire | Campo | Plumbing | P4 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2006 | 3 | 17280 | 2036 | 18 2036: 26092.8
Mountain Empire | Campo | Plumbing | P5 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2006 | 3 | 17280 | 2036 | 18 2036: 26092.8
Mountain Empire | Campo | Finishes | Classroom Building | Carpet Roll |  | 25287 | 7.9 | 15 | No | 1990 | 3 | 199767.3 | 2019 | 1 2019: 199767.3; 16 2034: 289662.585
Mountain Empire | Campo | Finishes | Classroom Building | Paint Exterior |  | 25287 | 1.6 | 10 | No | 1990 | 3 | 40459.2 | 2019 | 1 2019: 40459.2; 11 2029: 52596.96
Mountain Empire | Campo | Finishes | P1 | Custom Exterior |  | 960 | 6.5 | 20 | Yes | 2014 | 3 | 6240 | 2034 | 16 2034: 9048
Mountain Empire | Campo | Finishes | P2 | Custom Exterior |  | 960 | 6.5 | 20 | Yes | 2014 | 3 | 6240 | 2034 | 16 2034: 9048
Mountain Empire | Campo | Finishes | P3 | Custom Exterior |  | 960 | 6.5 | 20 | Yes | 2014 | 3 | 6240 | 2034 | 16 2034: 9048
Mountain Empire | Campo | Finishes | P4 | Custom Exterior |  | 960 | 6.5 | 20 | Yes | 2014 | 3 | 6240 | 2034 | 16 2034: 9048
Mountain Empire | Campo | Finishes | P5 | Custom Exterior |  | 960 | 6.5 | 20 | Yes | 2014 | 3 | 6240 | 2034 | 16 2034: 9048
Mountain Empire | Campo | Finishes | Classroom Building | Paint Interior |  | 25287 | 1.5 | 10 | No | 1990 | 3 | 37930.5 | 2019 | 1 2019: 37930.5; 11 2029: 49309.65
Mountain Empire | Campo | LowVoltage | Classroom Building | FACP |  | 1 | 20000 | 15 | No | 1990 | 3 | 20000 | 2019 | 1 2019: 20000; 16 2034: 29000
Mountain Empire | Campo | LowVoltage | Classroom Building | Clock/Bell/Paging |  | 1 | 40000 | 20 | No | 1990 | 3 | 40000 | 2019 | 1 2019: 40000
Mountain Empire | Campo | HVAC | P1 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Campo | HVAC | P2 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Campo | HVAC | P3 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Campo | HVAC | P4 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2006 | 3 | 12000 | 2021 | 3 2021: 12720; 18 2036: 18120
Mountain Empire | Campo | HVAC | P5 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2006 | 3 | 12000 | 2021 | 3 2021: 12720; 18 2036: 18120
Mountain Empire | Campo | Electrical | P1 | Panel 100A 208/120 3P |  | 1 | 8500 | 30 | Yes | 1992 | 3 | 8500 | 2022 | 4 2022: 9265
Mountain Empire | Campo | Electrical | P2 | Panel 100A 208/120 3P |  | 1 | 8500 | 30 | Yes | 1992 | 3 | 8500 | 2022 | 4 2022: 9265
Mountain Empire | Campo | Electrical | P3 | Panel 100A 208/120 3P |  | 1 | 8500 | 30 | Yes | 1992 | 3 | 8500 | 2022 | 4 2022: 9265
Mountain Empire | Campo | Electrical | P4 | Panel 100A 208/120 3P |  | 1 | 8500 | 30 | Yes | 2006 | 3 | 8500 | 2036 | 18 2036: 12835
Mountain Empire | Campo | Electrical | P5 | Panel 100A 208/120 3P |  | 1 | 8500 | 30 | Yes | 2006 | 3 | 8500 | 2036 | 18 2036: 12835
Mountain Empire | Campo | Electrical | Classroom Building | Fluorescent CR Lighting |  | 25287 | 4 | 20 | No | 1990 | 3 | 101148 | 2019 | 1 2019: 101148
Mountain Empire | Campo | Electrical | Classroom Building | Main Switch Board 1600A 208/120 3P 42,000AIC |  | 1 | 145000 | 30 | No | 1990 | 3 | 145000 | 2020 | 2 2020: 149350
Mountain Empire | Campo | Electrical | Classroom Building | Panel 400A 277/480 3P |  | 1 | 8500 | 30 | No | 1990 | 3 | 8500 | 2020 | 2 2020: 8755
Mountain Empire | Campo | Electrical | Classroom Building | Panel 400A 277/480 3P |  | 1 | 8500 | 30 | No | 1990 | 3 | 8500 | 2020 | 2 2020: 8755
Mountain Empire | Campo | Electrical | Classroom Building | Panel 225A 480/277 3P |  | 1 | 12500 | 30 | No | 1990 | 3 | 12500 | 2020 | 2 2020: 12875
Mountain Empire | Campo | Electrical | Classroom Building | Panel 225A 208/120 3P |  | 1 | 10500 | 30 | No | 1990 | 3 | 10500 | 2020 | 2 2020: 10815
Mountain Empire | Campo | Electrical | Classroom Building | Panel 225A 208/120 3P |  | 1 | 10500 | 30 | No | 1990 | 3 | 10500 | 2020 | 2 2020: 10815
Mountain Empire | Campo | Electrical | Classroom Building | Panel 225A 208/120 3P |  | 1 | 10500 | 30 | No | 1990 | 3 | 10500 | 2020 | 2 2020: 10815
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-1 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-2 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-3 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-4 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-5 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-6 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-7 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-8 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-9 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-10 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-11 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-12 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-13 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-14 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-15 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 5 Ton | PUT-CB-16 | 1 | 12500 | 15 | No | 1990 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 3.5 Ton | PUT-CB-17 | 1 | 8750 | 15 | No | 1990 | 3 | 8750 | 2019 | 1 2019: 8750; 16 2034: 12687.5
Mountain Empire | Campo | HVAC | Classroom Building | Package Unit 10 Ton | PUT-CB-18 | 1 | 25000 | 15 | No | 1990 | 3 | 25000 | 2019 | 1 2019: 25000; 16 2034: 36250
Mountain Empire | Campo | Electrical | Pump House | Panel 100A 208/120 3P | PP | 1 | 8500 | 30 | No | 1990 | 3 | 8500 | 2020 | 2 2020: 8755
Mountain Empire | Campo | Electrical | Pump House | Panel 100A 277/480 3P | PL | 1 | 8500 | 30 | No | 1990 | 3 | 8500 | 2020 | 2 2020: 8755
Mountain Empire | Campo | HVAC | South Wing | Package Unit 5 Ton | PUT-SW-1 | 1 | 12500 | 15 | No | 2004 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | South Wing | Package Unit 5 Ton | PUT-SW-2 | 1 | 12500 | 15 | No | 2004 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | South Wing | Package Unit 5 Ton | PUT-SW-3 | 1 | 12500 | 15 | No | 2004 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | South Wing | Package Unit 5 Ton | PUT-SW-4 | 1 | 12500 | 15 | No | 2004 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | South Wing | Package Unit 5 Ton | PUT-SW-5 | 1 | 12500 | 15 | No | 2004 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Campo | HVAC | South Wing | Package Unit 2.5 Ton | PUT-SW-6 | 1 | 6250 | 15 | No | 2004 | 3 | 6250 | 2019 | 1 2019: 6250; 16 2034: 9062.5
Mountain Empire | Campo | HVAC | South Wing | Package Unit 7.5 Ton | PUT-SW-7 | 1 | 18750 | 15 | No | 2004 | 3 | 18750 | 2019 | 1 2019: 18750; 16 2034: 27187.5
Mountain Empire | Campo | Electrical | South Wing | Panel 400A 277/480 3P | LB | 1 | 8500 | 30 | No | 2004 | 3 | 8500 | 2034 | 16 2034: 12325
Mountain Empire | Campo | Electrical | South Wing | Panel 225A 208/120 3P | PB-1 | 1 | 10500 | 30 | No | 2004 | 3 | 10500 | 2034 | 16 2034: 15225
Mountain Empire | Campo | Electrical | South Wing | Panel 100A 277/480 3P | LBB | 1 | 8500 | 30 | No | 2004 | 3 | 8500 | 2034 | 16 2034: 12325
Mountain Empire | Campo | Electrical | South Wing | Fluorescent CR Lighting |  | 8602 | 4 | 20 | No | 2004 | 3 | 34408 | 2024 | 6 2024: 39569.2
Mountain Empire | Campo | Finishes | South Wing | Carpet Roll |  | 8602 | 7.9 | 15 | No | 2004 | 3 | 67955.8 | 2019 | 1 2019: 67955.8; 16 2034: 98535.91
Mountain Empire | Campo | Finishes | South Wing | Paint Exterior |  | 8602 | 1.6 | 10 | No | 2004 | 3 | 13763.2 | 2019 | 1 2019: 13763.2; 11 2029: 17892.16
Mountain Empire | Campo | Plumbing | South Wing | DCW/Sewer |  | 8602 | 18 | 30 | No | 2004 | 3 | 154836 | 2034 | 16 2034: 224512.2
Mountain Empire | Campo | Roofing | South Wing | BUR - Gravel | South Wing | 7151 | 18 | 30 | No | 2004 | 3 | 128718 | 2034 | 16 2034: 186641.1
Mountain Empire | Campo | Roofing | South Wing | Ashpalt Shingle | SW Section A | 1181 | 9.5 | 15 | No | 2004 | 3 | 11219.5 | 2019 | 1 2019: 11219.5; 16 2034: 16268.275
Mountain Empire | Campo | Roofing | South Wing | Ashpalt Shingle | SW Section B | 256 | 9.5 | 15 | No | 2004 | 3 | 2432 | 2019 | 1 2019: 2432; 16 2034: 3526.4
Mountain Empire | Campo | Roofing | South Wing | Ashpalt Shingle | SW Section C | 614 | 9.5 | 15 | No | 2004 | 3 | 5833 | 2019 | 1 2019: 5833; 16 2034: 8457.85
Mountain Empire | Campo | Roofing | South Wing | Ashpalt Shingle | SW Section D | 54 | 9.5 | 15 | No | 2004 | 3 | 513 | 2019 | 1 2019: 513; 16 2034: 743.85
Mountain Empire | Campo | Finishes | South Wing | Paint Interior |  | 8602 | 1.5 | 10 | No | 2004 | 3 | 12903 | 2019 | 1 2019: 12903; 11 2029: 16773.9
Mountain Empire | Campo | Playground | Kinder Playground | Wood Fiber |  | 2860 | 3.15 | 5 | No | 2014 | 3 | 9009 | 2019 | 1 2019: 9009; 6 2024: 10360.35; 11 2029: 11711.7; 16 2034: 13063.05
Mountain Empire | Campo | Playground | Primary Playground | Wood Fiber |  | 5619 | 3.15 | 5 | No | 2014 | 3 | 17699.85 | 2019 | 1 2019: 17699.85; 6 2024: 20354.8275; 11 2029: 23009.805; 16 2034: 25664.7825
Mountain Empire | Campo | Playground | Swings | Wood Fiber |  | 3269 | 3.15 | 5 | No | 2014 | 3 | 10297.35 | 2019 | 1 2019: 10297.35; 6 2024: 11841.9525; 11 2029: 13386.555; 16 2034: 14931.1575
Mountain Empire | Campo | Finishes | P1 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1992 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Campo | Finishes | P1 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1992 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Campo | Electrical | P1 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1992 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | Campo | Electrical | P1 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1992 | 3 | 10500 | 2022 | 4 2022: 11445
Mountain Empire | Campo | Plumbing | P1 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1992 | 3 | 17280 | 2022 | 4 2022: 18835.2
Mountain Empire | Campo | Roofing | P1 | BUR - Gran Cap |  | 1130 | 15 | 25 | Yes | 1992 | 1 | 16950 | 2019 | 1 2019: 16950
Mountain Empire | Campo | Finishes | P2 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1992 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Campo | Finishes | P2 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1992 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Campo | Electrical | P2 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1992 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | Campo | Electrical | P2 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1992 | 3 | 10500 | 2022 | 4 2022: 11445
Mountain Empire | Campo | Plumbing | P2 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1992 | 3 | 17280 | 2022 | 4 2022: 18835.2
Mountain Empire | Campo | Roofing | P2 | Standing Seam |  | 1180 | 25 | 25 | Yes | 1992 | 1 | 29500 | 2019 | 1 2019: 29500
Mountain Empire | Campo | Finishes | P3 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1992 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Campo | Finishes | P3 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1992 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Campo | Electrical | P3 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1992 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | Campo | Electrical | P3 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1992 | 3 | 10500 | 2022 | 4 2022: 11445
Mountain Empire | Campo | Plumbing | P3 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1992 | 3 | 17280 | 2022 | 4 2022: 18835.2
Mountain Empire | Campo | Roofing | P3 | BUR - Gran Cap |  | 1209 | 15 | 25 | Yes | 1992 | 1 | 18135 | 2019 | 1 2019: 18135
Mountain Empire | Campo | Finishes | P4 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2006 | 3 | 7584 | 2021 | 3 2021: 8039.04; 18 2036: 11451.84
Mountain Empire | Campo | Finishes | P4 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2006 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Campo | Electrical | P4 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2006 | 3 | 3840 | 2026 | 8 2026: 4646.4
Mountain Empire | Campo | Electrical | P4 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2006 | 3 | 10500 | 2036 | 18 2036: 15855
Mountain Empire | Campo | Plumbing | P4 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2006 | 3 | 17280 | 2036 | 18 2036: 26092.8
Mountain Empire | Campo | Roofing | P4 | BUR - Gran Cap |  | 1178 | 15 | 25 | Yes | 2005 | 1 | 17670 | 2019 | 1 2019: 17670
Mountain Empire | Campo | Finishes | P5 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2006 | 3 | 7584 | 2021 | 3 2021: 8039.04; 18 2036: 11451.84
Mountain Empire | Campo | Finishes | P5 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2006 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Campo | Electrical | P5 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2006 | 3 | 3840 | 2026 | 8 2026: 4646.4
Mountain Empire | Campo | Electrical | P5 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2006 | 3 | 10500 | 2036 | 18 2036: 15855
Mountain Empire | Campo | Plumbing | P5 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2006 | 3 | 17280 | 2036 | 18 2036: 26092.8
Mountain Empire | Campo | Roofing | P5 | BUR - Gran Cap |  | 1114 | 15 | 25 | Yes | 2005 | 1 | 16710 | 2019 | 1 2019: 16710
Mountain Empire | Campo | Roofing | Pump House | BUR - Gran Cap |  | 348 | 15 | 25 | No | 1995 | 3 | 5220 | 2020 | 2 2020: 5376.6
Mountain Empire | Campo | Roofing | Shade Structure | Vinyl Fabric |  | 260 | 15 | 10 | No | 2006 | 3 | 3900 | 2019 | 1 2019: 3900; 11 2029: 5070
Mountain Empire | PineValley | Roofing | Building 1 | Poly Foam |  | 1205 | 10 | 10 | Yes | 2005 | 3 | 12050 | 2019 | 1 2019: 12050; 11 2029: 15665
Mountain Empire | PineValley | Roofing | Building 2 | Standing Seam |  | 2809 | 25 | 25 | Yes | 1980 | 1 | 70225 | 2019 | 1 2019: 70225
Mountain Empire | PineValley | Roofing | Building 3 | Standing Seam |  | 1120 | 25 | 25 | Yes | 2005 | 3 | 28000 | 2030 | 12 2030: 37240
Mountain Empire | PineValley | Roofing | Building 4 | BUR - Gran Cap |  | 1151 | 15 | 25 | Yes | 2005 | 3 | 17265 | 2030 | 12 2030: 22962.45
Mountain Empire | PineValley | Roofing | Building 5 | Standing Seam |  | 1111 | 25 | 25 | Yes | 1994 | 3 | 27775 | 2019 | 1 2019: 27775
Mountain Empire | PineValley | Roofing | Building 6 | Standing Seam |  | 1113 | 25 | 25 | Yes | 1989 | 3 | 27825 | 2019 | 1 2019: 27825
Mountain Empire | PineValley | Roofing | Building 7 | BUR - Gran Cap |  | 1145 | 15 | 25 | Yes | 1988 | 2 | 17175 | 2019 | 1 2019: 17175
Mountain Empire | PineValley | Roofing | Building 8 | BUR - Gran Cap |  | 1158 | 15 | 25 | Yes | 1988 | 2 | 17370 | 2019 | 1 2019: 17370
Mountain Empire | PineValley | Roofing | Restroom | BUR - Gran Cap |  | 611 | 15 | 25 | Yes | 1988 | 3 | 9165 | 2019 | 1 2019: 9165
Mountain Empire | PineValley | Roofing | Lunch Shelter | Vinyl Fabric |  | 517 | 15 | 10 | Yes | 2013 | 3 | 7755 | 2023 | 5 2023: 8685.6; 15 2033: 11012.1
Mountain Empire | PineValley | Finishes | Building 1 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1990 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | PineValley | Finishes | Building 2 | Carpet Roll |  | 2400 | 7.9 | 15 | Yes | 1990 | 3 | 18960 | 2019 | 1 2019: 18960; 16 2034: 27492
Mountain Empire | PineValley | Finishes | Building 3 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1990 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | PineValley | Finishes | Building 4 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1990 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | PineValley | Finishes | Building 5 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1990 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | PineValley | Finishes | Building 6 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1990 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | PineValley | Finishes | Building 7 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1990 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | PineValley | Finishes | Building 8 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1990 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | PineValley | Finishes | Building 1 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1980 | 1 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | PineValley | Finishes | Building 2 | Paint Exterior |  | 2400 | 1.6 | 10 | Yes | 1980 | 3 | 3840 | 2019 | 1 2019: 3840; 11 2029: 4992
Mountain Empire | PineValley | Finishes | Building 3 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1988 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | PineValley | Finishes | Building 4 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1988 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | PineValley | Finishes | Building 5 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1994 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | PineValley | Finishes | Building 6 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1989 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | PineValley | Finishes | Building 7 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1988 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | PineValley | Finishes | Building 8 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 1988 | 3 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | PineValley | Finishes | Building 1 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1980 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | PineValley | Finishes | Building 2 | Paint Interior |  | 2400 | 1.5 | 10 | Yes | 1980 | 3 | 3600 | 2019 | 1 2019: 3600; 11 2029: 4680
Mountain Empire | PineValley | Finishes | Building 3 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1988 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | PineValley | Finishes | Building 4 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1988 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | PineValley | Finishes | Building 5 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1994 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | PineValley | Finishes | Building 6 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1989 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | PineValley | Finishes | Building 7 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1988 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | PineValley | Finishes | Building 8 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1988 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | PineValley | Plumbing | Building 1 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1980 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | PineValley | Plumbing | Building 2 | DCW/Sewer |  | 2400 | 18 | 30 | Yes | 1980 | 3 | 43200 | 2019 | 1 2019: 43200
Mountain Empire | PineValley | Plumbing | Building 3 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1988 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | PineValley | Plumbing | Building 4 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1988 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | PineValley | Plumbing | Building 5 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1994 | 3 | 17280 | 2024 | 6 2024: 19872
Mountain Empire | PineValley | Plumbing | Building 6 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1989 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | PineValley | Plumbing | Building 7 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1988 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | PineValley | Plumbing | Building 8 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1988 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | PineValley | Plumbing | Restroom | DCW/Sewer |  | 611 | 18 | 30 | Yes | 1988 | 3 | 10998 | 2019 | 1 2019: 10998
Mountain Empire | PineValley | Electrical | Building 1 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1980 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | PineValley | Electrical | Building 2 | Fluorescent CR Lighting |  | 2400 | 4 | 20 | Yes | 1980 | 3 | 9600 | 2019 | 1 2019: 9600
Mountain Empire | PineValley | Electrical | Building 3 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1988 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | PineValley | Electrical | Building 4 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1988 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | PineValley | Electrical | Building 5 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1994 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | PineValley | Electrical | Building 6 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1989 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | PineValley | Electrical | Building 7 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1988 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | PineValley | Electrical | Building 8 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1988 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | PineValley | Finishes | Restroom | Vinyl Sheet |  | 611 | 9.75 | 12 | Yes | 1988 | 3 | 5957.25 | 2019 | 1 2019: 5957.25; 13 2031: 8101.86
Mountain Empire | PineValley | Finishes | Restroom | Paint Exterior |  | 611 | 1.6 | 10 | Yes | 1988 | 1 | 977.6 | 2019 | 1 2019: 977.6; 11 2029: 1270.88
Mountain Empire | PineValley | Finishes | Restroom | Paint Interior |  | 611 | 1.5 | 10 | Yes | 1988 | 1 | 916.5 | 2019 | 1 2019: 916.5; 11 2029: 1191.45
Mountain Empire | PineValley | Electrical | Building 1 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1980 | 3 | 10500 | 2019 | 1 2019: 10500
Mountain Empire | PineValley | Electrical | Building 2 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1980 | 3 | 10500 | 2019 | 1 2019: 10500
Mountain Empire | PineValley | Electrical | Building 3 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1988 | 3 | 10500 | 2019 | 1 2019: 10500
Mountain Empire | PineValley | Electrical | Building 4 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1988 | 3 | 10500 | 2019 | 1 2019: 10500
Mountain Empire | PineValley | Electrical | Building 5 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1994 | 3 | 10500 | 2024 | 6 2024: 12075
Mountain Empire | PineValley | Electrical | Building 6 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1989 | 3 | 10500 | 2019 | 1 2019: 10500
Mountain Empire | PineValley | Electrical | Building 7 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1988 | 3 | 10500 | 2019 | 1 2019: 10500
Mountain Empire | PineValley | Electrical | Building 8 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1988 | 3 | 10500 | 2019 | 1 2019: 10500
Mountain Empire | PineValley | Paving | Parking Lot | Asphalt Parking Lot |  | 5910 | 7.5 | 30 | Yes | 1980 | 1 | 44325 | 2019 | 1 2019: 44325
Mountain Empire | PineValley | Paving | Blacktop | Asphalt Playground |  | 12435 | 5.5 | 30 | Yes | 2010 | 3 | 68392.5 | 2040
Mountain Empire | PineValley | Playground | Playground | Wood Fiber |  | 2630 | 3.15 | 5 | Yes | 2003 | 3 | 8284.5 | 2019 | 1 2019: 8284.5; 6 2024: 9527.175; 11 2029: 10769.85; 16 2034: 12012.525
Mountain Empire | PineValley | Playground | Swings | Wood Fiber |  | 3290 | 3.15 | 5 | Yes | 2003 | 3 | 10363.5 | 2019 | 1 2019: 10363.5; 6 2024: 11918.025; 11 2029: 13472.55; 16 2034: 15027.075
Mountain Empire | PineValley | Paving | Parking Lot | Seal Coat and Stripe |  | 5910 | 0.35 | 5 | Yes | 2014 | 3 | 2068.5 | 2019 | 1 2019: 2068.5; 6 2024: 2378.775; 11 2029: 2689.05; 16 2034: 2999.325
Mountain Empire | PineValley | Paving | Blacktop | Seal Coat and Stripe |  | 12435 | 0.35 | 5 | Yes | 2010 | 3 | 4352.25 | 2019 | 1 2019: 4352.25; 6 2024: 5005.0875; 11 2029: 5657.925; 16 2034: 6310.7625
Mountain Empire | PineValley | HVAC | Building 1 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | HVAC | Building 2 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | HVAC | Building 3 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | HVAC | Building 4 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | HVAC | Building 5 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | HVAC | Building 6 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | HVAC | Building 7 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | HVAC | Building 8 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | HVAC | Building 2 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | HVAC | Building 2 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | HVAC | Building 2 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | HVAC | Building 1 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | PineValley | LowVoltage |  | FACP |  | 1 | 20000 | 15 | Yes | 1980 | 3 | 20000 | 2019 | 1 2019: 20000; 16 2034: 29000
Mountain Empire | PineValley | LowVoltage |  | Clock/Bell/Paging |  | 1 | 40000 | 20 | Yes | 1980 | 3 | 40000 | 2019 | 1 2019: 40000
Mountain Empire | PineValley | Fencing |  | 2" Chain Link, Galv, 6' |  | 1269 | 22.5 | 15 | No | 1980 | 3 | 28552.5 | 2019 | 1 2019: 28552.5; 16 2034: 41401.125
Mountain Empire | Jacumba | Roofing | Building A | BUR - Gran Cap | A | 3380 | 15 | 25 | No | 1980 | 3 | 50700 | 2019 | 1 2019: 50700
Mountain Empire | Jacumba | Roofing | Building A | Ashpalt Shingle | A2 | 854 | 9.5 | 15 | No | 2005 | 3 | 8113 | 2020 | 2 2020: 8356.39; 17 2035: 12007.24
Mountain Empire | Jacumba | Roofing | Building A | BUR - Gran Cap | A3 | 237 | 15 | 25 | No | 2005 | 3 | 3555 | 2030 | 12 2030: 4728.15
Mountain Empire | Jacumba | Roofing | Building A | BUR - Gran Cap | A1 | 94 | 15 | 25 | No | 1990 | 3 | 1410 | 2019 | 1 2019: 1410
Mountain Empire | Jacumba | Roofing | Office | SP - TPO |  | 632 | 12 | 10 | Yes | 1980 | 2 | 7584 | 2019 | 1 2019: 7584; 11 2029: 9859.2
Mountain Empire | Jacumba | Roofing | Restroom | BUR - Gran Cap |  | 624 | 15 | 25 | Yes | 2000 | 3 | 9360 | 2025 | 7 2025: 11044.8
Mountain Empire | Jacumba | Roofing | ASP | BUR - Gran Cap |  | 1118 | 15 | 25 | Yes | 2007 | 3 | 16770 | 2032 | 14 2032: 23310.3
Mountain Empire | Jacumba | Paving | AC Sidewalk | Asphalt Playground |  | 2777 | 5.5 | 30 | No | 2000 | 1 | 15273.5 | 2019 | 1 2019: 15273.5
Mountain Empire | Jacumba | Paving | Blacktop | Asphalt Playground |  | 7669 | 5.5 | 30 | No | 2000 | 1 | 42179.5 | 2019 | 1 2019: 42179.5
Mountain Empire | Jacumba | Paving | Parking Lot | Asphalt Parking Lot |  | 5019 | 7.5 | 30 | No | 2000 | 1 | 37642.5 | 2019 | 1 2019: 37642.5
Mountain Empire | Jacumba | Paving | AC Sidewalk | Seal Coat and Stripe |  | 2777 | 0.35 | 5 | No | 2005 | 1 | 971.95 | 2019 | 1 2019: 971.95; 6 2024: 1117.7425; 11 2029: 1263.535; 16 2034: 1409.3275
Mountain Empire | Jacumba | Paving | Blacktop | Seal Coat and Stripe |  | 7669 | 0.35 | 5 | No | 2005 | 1 | 2684.15 | 2019 | 1 2019: 2684.15; 6 2024: 3086.7725; 11 2029: 3489.395; 16 2034: 3892.0175
Mountain Empire | Jacumba | Paving | Parking Lot | Seal Coat and Stripe |  | 5019 | 0.35 | 5 | No | 2005 | 1 | 1756.65 | 2019 | 1 2019: 1756.65; 6 2024: 2020.1475; 11 2029: 2283.645; 16 2034: 2547.1425
Mountain Empire | Jacumba | Paving | PC Basketball Court | PC Sidewalk (Non-reinforced) |  | 2149 | 6.5 | 30 | No | 1995 | 1 | 13968.5 | 2019 | 1 2019: 13968.5
Mountain Empire | Jacumba | Fencing | Perimeter Fence | 2" Chain Link, Galv, 6' |  | 1098 | 22.5 | 15 | No | 2000 | 3 | 24705 | 2019 | 1 2019: 24705; 16 2034: 35822.25
Mountain Empire | Jacumba | Playground | Playground | Wood Fiber |  | 9629 | 3.15 | 5 | No | 2003 | 3 | 30331.35 | 2019 | 1 2019: 30331.35; 6 2024: 34881.0525; 11 2029: 39430.755; 16 2034: 43980.4575
Mountain Empire | Jacumba | LowVoltage |  | FACP |  | 1 | 20000 | 15 | No | 2000 | 3 | 20000 | 2019 | 1 2019: 20000; 16 2034: 29000
Mountain Empire | Jacumba | LowVoltage |  | Clock/Bell/Paging |  | 1 | 40000 | 20 | No | 2000 | 3 | 40000 | 2020 | 2 2020: 41200
Mountain Empire | Jacumba | Fencing | Perimeter Fence | 2" Chain Link, Galv, 6' | Trash Enclosure | 40 | 22.5 | 15 | No | 1995 | 3 | 900 | 2019 | 1 2019: 900; 16 2034: 1305
Mountain Empire | Jacumba | Finishes | ASP | Vinyl Sheet |  | 960 | 9.75 | 12 | Yes | 2013 | 3 | 9360 | 2025 | 7 2025: 11044.8; 19 2037: 14414.4
Mountain Empire | Jacumba | Finishes | Building A | Carpet Roll |  | 3498 | 7.9 | 15 | No | 1990 | 3 | 27634.2 | 2019 | 1 2019: 27634.2; 16 2034: 40069.59
Mountain Empire | Jacumba | Finishes | Office | Carpet Roll |  | 580 | 7.9 | 15 | Yes | 1990 | 3 | 4582 | 2019 | 1 2019: 4582; 16 2034: 6643.9
Mountain Empire | Jacumba | Finishes | Restroom | Vinyl Sheet |  | 480 | 9.75 | 12 | Yes | 1990 | 3 | 4680 | 2019 | 1 2019: 4680; 13 2031: 6364.8
Mountain Empire | Jacumba | Finishes | ASP | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2012 | 3 | 1536 | 2022 | 4 2022: 1674.24; 14 2032: 2135.04
Mountain Empire | Jacumba | Finishes | Building A | Paint Exterior |  | 3498 | 1.6 | 10 | No | 2012 | 3 | 5596.8 | 2022 | 4 2022: 6100.512; 14 2032: 7779.552
Mountain Empire | Jacumba | Finishes | Office | Paint Exterior |  | 580 | 1.6 | 10 | Yes | 2012 | 3 | 928 | 2022 | 4 2022: 1011.52; 14 2032: 1289.92
Mountain Empire | Jacumba | Finishes | Restroom | Paint Exterior |  | 480 | 1.6 | 10 | Yes | 2012 | 3 | 768 | 2022 | 4 2022: 837.12; 14 2032: 1067.52
Mountain Empire | Jacumba | Finishes | ASP | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2000 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Jacumba | Finishes | Building A | Paint Interior |  | 3498 | 1.5 | 10 | No | 2000 | 3 | 5247 | 2019 | 1 2019: 5247; 11 2029: 6821.1
Mountain Empire | Jacumba | Finishes | Office | Paint Interior |  | 580 | 1.5 | 10 | Yes | 2000 | 3 | 870 | 2019 | 1 2019: 870; 11 2029: 1131
Mountain Empire | Jacumba | Finishes | Restroom | Paint Interior |  | 480 | 1.5 | 10 | Yes | 2000 | 3 | 720 | 2019 | 1 2019: 720; 11 2029: 936
Mountain Empire | Jacumba | Plumbing | ASP | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2000 | 3 | 17280 | 2030 | 12 2030: 22982.4
Mountain Empire | Jacumba | Plumbing | Building A | DCW/Sewer |  | 3498 | 18 | 30 | No | 1947 | 3 | 62964 | 2019 | 1 2019: 62964
Mountain Empire | Jacumba | Plumbing | Office | DCW/Sewer |  | 580 | 18 | 30 | Yes | 2000 | 3 | 10440 | 2030 | 12 2030: 13885.2
Mountain Empire | Jacumba | Plumbing | Restroom | DCW/Sewer |  | 480 | 18 | 30 | Yes | 2000 | 3 | 8640 | 2030 | 12 2030: 11491.2
Mountain Empire | Jacumba | Electrical | ASP | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2000 | 3 | 3840 | 2020 | 2 2020: 3955.2
Mountain Empire | Jacumba | Electrical | Building A | Fluorescent CR Lighting |  | 3498 | 4 | 20 | No | 2000 | 3 | 13992 | 2020 | 2 2020: 14411.76
Mountain Empire | Jacumba | Electrical | Office | Fluorescent CR Lighting |  | 580 | 4 | 20 | Yes | 2000 | 3 | 2320 | 2020 | 2 2020: 2389.6
Mountain Empire | Jacumba | Electrical | Restroom | Fluorescent CR Lighting |  | 480 | 4 | 20 | Yes | 2000 | 3 | 1920 | 2020 | 2 2020: 1977.6
Mountain Empire | Jacumba | Electrical | ASP | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | Jacumba | Electrical | Building A | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | No | 1995 | 3 | 10500 | 2025 | 7 2025: 12390
Mountain Empire | Jacumba | Electrical | Office | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | Jacumba | Electrical | Restroom | Panel 100A 208/120 3P |  | 1 | 8500 | 30 | Yes | 2000 | 3 | 8500 | 2030 | 12 2030: 11305
Mountain Empire | Jacumba | HVAC | Restroom | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Jacumba | HVAC | Office | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Jacumba | HVAC | ASP | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Jacumba | HVAC | ASP | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Jacumba | HVAC | Building A | Package Unit 5 Ton |  | 1 | 12500 | 15 | No | 1991 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Jacumba | HVAC | Building A | Package Unit 5 Ton |  | 1 | 12500 | 15 | No | 1991 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Jacumba | HVAC | Building A | Package Unit 5 Ton |  | 1 | 12500 | 15 | No | 1991 | 3 | 12500 | 2019 | 1 2019: 12500; 16 2034: 18125
Mountain Empire | Potrero | Roofing | MS1 | Standing Seam |  | 1132 | 25 | 25 | Yes | 2009 | 3 | 28300 | 2034 | 16 2034: 41035
Mountain Empire | Potrero | Roofing | MS2 | Standing Seam |  | 1136 | 25 | 25 | Yes | 2009 | 3 | 28400 | 2034 | 16 2034: 41180
Mountain Empire | Potrero | Roofing | MS3 | Standing Seam |  | 1146 | 25 | 25 | Yes | 2009 | 3 | 28650 | 2034 | 16 2034: 41542.5
Mountain Empire | Potrero | Roofing | Upper Restroom | Standing Seam |  | 549 | 25 | 25 | Yes | 2009 | 3 | 13725 | 2034 | 16 2034: 19901.25
Mountain Empire | Potrero | Roofing | 4Plex | BUR - Gran Cap |  | 5031 | 15 | 25 | Yes | 1991 | 2 | 75465 | 2019 | 1 2019: 75465
Mountain Empire | Potrero | Roofing | Building 2 | BUR - Gran Cap |  | 1136 | 15 | 25 | Yes | 1986 | 1 | 17040 | 2019 | 1 2019: 17040
Mountain Empire | Potrero | Roofing | Building 3 | Standing Seam |  | 1200 | 25 | 25 | Yes | 2001 | 3 | 30000 | 2026 | 8 2026: 36300
Mountain Empire | Potrero | Roofing | Building 4 | Standing Seam |  | 1202 | 25 | 25 | Yes | 2001 | 3 | 30050 | 2026 | 8 2026: 36360.5
Mountain Empire | Potrero | Roofing | Building 5 | BUR - Gran Cap |  | 1161 | 15 | 25 | Yes | 2003 | 3 | 17415 | 2028 | 10 2028: 22117.05
Mountain Empire | Potrero | Roofing | Building 6 | Standing Seam |  | 1178 | 25 | 25 | Yes | 2009 | 3 | 29450 | 2034 | 16 2034: 42702.5
Mountain Empire | Potrero | Roofing | Building 7 | BUR - Gran Cap |  | 2182 | 15 | 25 | No | 1995 | 2 | 32730 | 2019 | 1 2019: 32730
Mountain Empire | Potrero | Roofing | Building 8 | BUR - Gran Cap |  | 855 | 15 | 25 | No | 1995 | 2 | 12825 | 2019 | 1 2019: 12825
Mountain Empire | Potrero | Roofing | Building 9 | BUR - Gran Cap |  | 896 | 15 | 25 | No | 1995 | 2 | 13440 | 2019 | 1 2019: 13440
Mountain Empire | Potrero | Roofing | Building 10 | BUR - Gran Cap |  | 1187 | 15 | 25 | Yes | 1986 | 2 | 17805 | 2019 | 1 2019: 17805
Mountain Empire | Potrero | Roofing | Building 11 | Standing Seam |  | 1142 | 25 | 25 | Yes | 2009 | 3 | 28550 | 2034 | 16 2034: 41397.5
Mountain Empire | Potrero | Roofing | Computer Lab | Standing Seam |  | 1783 | 25 | 25 | Yes | 2003 | 3 | 44575 | 2028 | 10 2028: 56610.25
Mountain Empire | Potrero | Roofing | Speech Center | BUR - Gran Cap |  | 656 | 15 | 25 | Yes | 1991 | 1 | 9840 | 2019 | 1 2019: 9840
Mountain Empire | Potrero | Roofing | Lower Restroom | BUR - Gran Cap |  | 518 | 15 | 25 | Yes | 2009 | 3 | 7770 | 2034 | 16 2034: 11266.5
Mountain Empire | Potrero | Roofing | Office | BUR - Gran Cap |  | 1661 | 15 | 25 | Yes | 1990 | 2 | 24915 | 2019 | 1 2019: 24915
Mountain Empire | Potrero | Roofing | Shade Shelter (North) | Vinyl Fabric |  | 339 | 15 | 10 | Yes | 2003 | 3 | 5085 | 2019 | 1 2019: 5085; 11 2029: 6610.5
Mountain Empire | Potrero | Roofing | Shade Shelter (South) | Vinyl Fabric |  | 856 | 15 | 10 | Yes | 2005 | 3 | 12840 | 2019 | 1 2019: 12840; 11 2029: 16692
Mountain Empire | Potrero | Roofing | Preschool | BUR - Gran Cap |  | 1876 | 15 | 25 | Yes | 2002 | 3 | 28140 | 2027 | 9 2027: 34893.6
Mountain Empire | Potrero | Finishes | MS1 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2009 | 2 | 7584 | 2021 | 3 2021: 8039.04; 18 2036: 11451.84
Mountain Empire | Potrero | Finishes | MS2 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2009 | 2 | 7584 | 2021 | 3 2021: 8039.04; 18 2036: 11451.84
Mountain Empire | Potrero | Finishes | MS3 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2009 | 2 | 7584 | 2021 | 3 2021: 8039.04; 18 2036: 11451.84
Mountain Empire | Potrero | Finishes | Upper Restroom | Vinyl Sheet |  | 400 | 9.75 | 12 | Yes | 2009 | 3 | 3900 | 2021 | 3 2021: 4134; 15 2033: 5538
Mountain Empire | Potrero | Finishes | 4Plex | Carpet Roll |  | 4200 | 7.9 | 15 | Yes | 1991 | 2 | 33180 | 2019 | 1 2019: 33180; 16 2034: 48111
Mountain Empire | Potrero | Finishes | Building 2 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1986 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Potrero | Finishes | Building 3 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2001 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Potrero | Finishes | Building 4 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2001 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Potrero | Finishes | Building 5 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2009 | 2 | 7584 | 2021 | 3 2021: 8039.04; 18 2036: 11451.84
Mountain Empire | Potrero | Finishes | Building 6 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2009 | 2 | 7584 | 2021 | 3 2021: 8039.04; 18 2036: 11451.84
Mountain Empire | Potrero | Finishes | Building 7 | Carpet Roll |  | 1920 | 7.9 | 15 | No | 1995 | 2 | 15168 | 2019 | 1 2019: 15168; 16 2034: 21993.6
Mountain Empire | Potrero | Finishes | Building 8 | Carpet Roll |  | 960 | 7.9 | 15 | No | 1995 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Potrero | Finishes | Building 9 | Carpet Roll |  | 960 | 7.9 | 15 | No | 1995 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Potrero | Finishes | Building 10 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1986 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Potrero | Finishes | Building 11 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2009 | 2 | 7584 | 2021 | 3 2021: 8039.04; 18 2036: 11451.84
Mountain Empire | Potrero | Finishes | Computer Lab | Carpet Roll |  | 1440 | 7.9 | 15 | Yes | 2003 | 2 | 11376 | 2019 | 1 2019: 11376; 16 2034: 16495.2
Mountain Empire | Potrero | Finishes | Speech Center | Carpet Roll |  | 650 | 7.9 | 15 | Yes | 1991 | 2 | 5135 | 2019 | 1 2019: 5135; 16 2034: 7445.75
Mountain Empire | Potrero | Finishes | Lower Restroom | Vinyl Sheet |  | 400 | 9.75 | 12 | Yes | 2015 | 3 | 3900 | 2027 | 9 2027: 4836
Mountain Empire | Potrero | Finishes | Office | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2002 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Potrero | Finishes | Preschool | Carpet Roll |  | 1440 | 7.9 | 15 | Yes | 2002 | 2 | 11376 | 2019 | 1 2019: 11376; 16 2034: 16495.2
Mountain Empire | Potrero | Finishes | MS1 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | MS2 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | MS3 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | Upper Restroom | Paint Exterior |  | 400 | 1.6 | 10 | Yes | 2014 | 3 | 640 | 2024 | 6 2024: 736; 16 2034: 928
Mountain Empire | Potrero | Finishes | 4Plex | Paint Exterior |  | 4200 | 1.6 | 10 | Yes | 2014 | 3 | 6720 | 2024 | 6 2024: 7728; 16 2034: 9744
Mountain Empire | Potrero | Finishes | Building 2 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | Building 3 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | Building 4 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | Building 5 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | Building 6 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | Building 7 | Paint Exterior |  | 1920 | 1.6 | 10 | No | 2014 | 3 | 3072 | 2024 | 6 2024: 3532.8; 16 2034: 4454.4
Mountain Empire | Potrero | Finishes | Building 8 | Paint Exterior |  | 960 | 1.6 | 10 | No | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | Building 9 | Paint Exterior |  | 960 | 1.6 | 10 | No | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | Building 10 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | Building 11 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | Computer Lab | Paint Exterior |  | 1440 | 1.6 | 10 | Yes | 2014 | 3 | 2304 | 2024 | 6 2024: 2649.6; 16 2034: 3340.8
Mountain Empire | Potrero | Finishes | Speech Center | Paint Exterior |  | 650 | 1.6 | 10 | Yes | 2014 | 3 | 1040 | 2024 | 6 2024: 1196; 16 2034: 1508
Mountain Empire | Potrero | Finishes | Lower Restroom | Paint Exterior |  | 400 | 1.6 | 10 | Yes | 2014 | 3 | 640 | 2024 | 6 2024: 736; 16 2034: 928
Mountain Empire | Potrero | Finishes | Office | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | Potrero | Finishes | Preschool | Paint Exterior |  | 1440 | 1.6 | 10 | Yes | 2014 | 3 | 2304 | 2024 | 6 2024: 2649.6; 16 2034: 3340.8
Mountain Empire | Potrero | Finishes | MS1 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2009 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | MS2 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2009 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | MS3 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2009 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | Upper Restroom | Paint Interior |  | 400 | 1.5 | 10 | Yes | 2009 | 2 | 600 | 2019 | 1 2019: 600; 11 2029: 780
Mountain Empire | Potrero | Finishes | 4Plex | Paint Interior |  | 4200 | 1.5 | 10 | Yes | 1991 | 2 | 6300 | 2019 | 1 2019: 6300; 11 2029: 8190
Mountain Empire | Potrero | Finishes | Building 2 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1986 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | Building 3 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2001 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | Building 4 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2001 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | Building 5 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2009 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | Building 6 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2009 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | Building 7 | Paint Interior |  | 1920 | 1.5 | 10 | No | 1995 | 2 | 2880 | 2019 | 1 2019: 2880; 11 2029: 3744
Mountain Empire | Potrero | Finishes | Building 8 | Paint Interior |  | 960 | 1.5 | 10 | No | 1995 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | Building 9 | Paint Interior |  | 960 | 1.5 | 10 | No | 1995 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | Building 10 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1986 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | Building 11 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2009 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | Computer Lab | Paint Interior |  | 1440 | 1.5 | 10 | Yes | 2003 | 2 | 2160 | 2019 | 1 2019: 2160; 11 2029: 2808
Mountain Empire | Potrero | Finishes | Speech Center | Paint Interior |  | 650 | 1.5 | 10 | Yes | 1991 | 2 | 975 | 2019 | 1 2019: 975; 11 2029: 1267.5
Mountain Empire | Potrero | Finishes | Lower Restroom | Paint Interior |  | 400 | 1.5 | 10 | Yes | 2000 | 2 | 600 | 2019 | 1 2019: 600; 11 2029: 780
Mountain Empire | Potrero | Finishes | Office | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2002 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Potrero | Finishes | Preschool | Paint Interior |  | 1440 | 1.5 | 10 | Yes | 2002 | 2 | 2160 | 2019 | 1 2019: 2160; 11 2029: 2808
Mountain Empire | Potrero | Plumbing | MS1 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2009 | 3 | 17280 | 2039
Mountain Empire | Potrero | Plumbing | MS2 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2009 | 3 | 17280 | 2039
Mountain Empire | Potrero | Plumbing | MS3 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2009 | 3 | 17280 | 2039
Mountain Empire | Potrero | Plumbing | Upper Restroom | DCW/Sewer |  | 400 | 18 | 30 | Yes | 2009 | 3 | 7200 | 2039
Mountain Empire | Potrero | Plumbing | 4Plex | DCW/Sewer |  | 4200 | 18 | 30 | Yes | 1991 | 3 | 75600 | 2021 | 3 2021: 80136
Mountain Empire | Potrero | Plumbing | Building 2 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1986 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | Potrero | Plumbing | Building 3 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2001 | 3 | 17280 | 2031 | 13 2031: 23500.8
Mountain Empire | Potrero | Plumbing | Building 4 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2001 | 3 | 17280 | 2031 | 13 2031: 23500.8
Mountain Empire | Potrero | Plumbing | Building 5 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2009 | 3 | 17280 | 2039
Mountain Empire | Potrero | Plumbing | Building 6 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2009 | 3 | 17280 | 2039
Mountain Empire | Potrero | Plumbing | Building 7 | DCW/Sewer |  | 1920 | 18 | 30 | No | 1995 | 3 | 34560 | 2025 | 7 2025: 40780.8
Mountain Empire | Potrero | Plumbing | Building 8 | DCW/Sewer |  | 960 | 18 | 30 | No | 1995 | 3 | 17280 | 2025 | 7 2025: 20390.4
Mountain Empire | Potrero | Plumbing | Building 9 | DCW/Sewer |  | 960 | 18 | 30 | No | 1995 | 3 | 17280 | 2025 | 7 2025: 20390.4
Mountain Empire | Potrero | Plumbing | Building 10 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1986 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | Potrero | Plumbing | Building 11 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2009 | 3 | 17280 | 2039
Mountain Empire | Potrero | Plumbing | Computer Lab | DCW/Sewer |  | 1440 | 18 | 30 | Yes | 2003 | 3 | 25920 | 2033 | 15 2033: 36806.4
Mountain Empire | Potrero | Plumbing | Speech Center | DCW/Sewer |  | 650 | 18 | 30 | Yes | 1991 | 3 | 11700 | 2021 | 3 2021: 12402
Mountain Empire | Potrero | Plumbing | Lower Restroom | DCW/Sewer |  | 400 | 18 | 30 | Yes | 2000 | 3 | 7200 | 2030 | 12 2030: 9576
Mountain Empire | Potrero | Plumbing | Office | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2002 | 3 | 17280 | 2032 | 14 2032: 24019.2
Mountain Empire | Potrero | Plumbing | Preschool | DCW/Sewer |  | 1440 | 18 | 30 | Yes | 2002 | 3 | 25920 | 2032 | 14 2032: 36028.8
Mountain Empire | Potrero | Electrical | MS1 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2009 | 3 | 3840 | 2029 | 11 2029: 4992
Mountain Empire | Potrero | Electrical | MS2 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2009 | 3 | 3840 | 2029 | 11 2029: 4992
Mountain Empire | Potrero | Electrical | MS3 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2009 | 3 | 3840 | 2029 | 11 2029: 4992
Mountain Empire | Potrero | Electrical | Upper Restroom | Fluorescent CR Lighting |  | 400 | 4 | 20 | Yes | 2009 | 3 | 1600 | 2029 | 11 2029: 2080
Mountain Empire | Potrero | Electrical | 4Plex | Fluorescent CR Lighting |  | 4200 | 4 | 20 | Yes | 1991 | 3 | 16800 | 2019 | 1 2019: 16800
Mountain Empire | Potrero | Electrical | Building 2 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1986 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | Potrero | Electrical | Building 3 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2001 | 3 | 3840 | 2021 | 3 2021: 4070.4
Mountain Empire | Potrero | Electrical | Building 4 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2001 | 3 | 3840 | 2021 | 3 2021: 4070.4
Mountain Empire | Potrero | Electrical | Building 5 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2009 | 3 | 3840 | 2029 | 11 2029: 4992
Mountain Empire | Potrero | Electrical | Building 6 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2009 | 3 | 3840 | 2029 | 11 2029: 4992
Mountain Empire | Potrero | Electrical | Building 7 | Fluorescent CR Lighting |  | 1920 | 4 | 20 | No | 1995 | 3 | 7680 | 2019 | 1 2019: 7680
Mountain Empire | Potrero | Electrical | Building 8 | Fluorescent CR Lighting |  | 960 | 4 | 20 | No | 1995 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | Potrero | Electrical | Building 9 | Fluorescent CR Lighting |  | 960 | 4 | 20 | No | 1995 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | Potrero | Electrical | Building 10 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1986 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | Potrero | Electrical | Building 11 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2009 | 3 | 3840 | 2029 | 11 2029: 4992
Mountain Empire | Potrero | Electrical | Computer Lab | Fluorescent CR Lighting |  | 1440 | 4 | 20 | Yes | 2003 | 3 | 5760 | 2023 | 5 2023: 6451.2
Mountain Empire | Potrero | Electrical | Speech Center | Fluorescent CR Lighting |  | 650 | 4 | 20 | Yes | 1991 | 3 | 2600 | 2019 | 1 2019: 2600
Mountain Empire | Potrero | Electrical | Lower Restroom | Fluorescent CR Lighting |  | 400 | 4 | 20 | Yes | 2000 | 3 | 1600 | 2020 | 2 2020: 1648
Mountain Empire | Potrero | Electrical | Office | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2002 | 3 | 3840 | 2022 | 4 2022: 4185.6
Mountain Empire | Potrero | Electrical | Preschool | Fluorescent CR Lighting |  | 1440 | 4 | 20 | Yes | 2002 | 3 | 5760 | 2022 | 4 2022: 6278.4
Mountain Empire | Potrero | LowVoltage |  | FACP |  | 1 | 20000 | 15 | Yes | 2000 | 3 | 20000 | 2019 | 1 2019: 20000; 16 2034: 29000
Mountain Empire | Potrero | LowVoltage |  | Clock/Bell/Paging |  | 1 | 40000 | 20 | Yes | 2000 | 3 | 40000 | 2020 | 2 2020: 41200
Mountain Empire | Potrero | HVAC | 4Plex | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | 4Plex | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | 4Plex | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | 4Plex | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | 4Plex | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | 4Plex | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | 4Plex | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | 4Plex | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | MS1 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | MS2 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | MS3 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Computer Lab | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 1 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | Potrero | HVAC | Building 10 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Building 11 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Speech Center | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Building 6 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 1 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | Potrero | HVAC | Building 5 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Building 4 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Building 3 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Building 2 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Building 9 | Heat Pump |  | 1 | 12000 | 15 | No | 1995 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | Potrero | HVAC | Building 9 | Heat Pump |  | 1 | 12000 | 15 | No | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Building 8 | Heat Pump |  | 1 | 12000 | 15 | No | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Building 8 | Heat Pump |  | 1 | 12000 | 15 | No | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Building 7 | Heat Pump |  | 1 | 12000 | 15 | No | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Building 7 | Heat Pump |  | 1 | 12000 | 15 | No | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Office | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Office | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | HVAC | Preschool | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Potrero | Electrical | MS1 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2009 | 3 | 10500 | 2039
Mountain Empire | Potrero | Electrical | MS2 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2009 | 3 | 10500 | 2039
Mountain Empire | Potrero | Electrical | MS3 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2009 | 3 | 10500 | 2039
Mountain Empire | Potrero | Electrical | Upper Restroom | Panel 100A 208/120 3P |  | 1 | 8500 | 30 | Yes | 2009 | 3 | 8500 | 2039
Mountain Empire | Potrero | Electrical | 4Plex | Panel 200A 208/120 3P |  | 2 | 10500 | 30 | Yes | 1991 | 3 | 21000 | 2021 | 3 2021: 22260
Mountain Empire | Potrero | Electrical | Building 2 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1986 | 3 | 10500 | 2019 | 1 2019: 10500
Mountain Empire | Potrero | Electrical | Building 3 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2001 | 3 | 10500 | 2031 | 13 2031: 14280
Mountain Empire | Potrero | Electrical | Building 4 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2001 | 3 | 10500 | 2031 | 13 2031: 14280
Mountain Empire | Potrero | Electrical | Building 5 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2009 | 3 | 10500 | 2039
Mountain Empire | Potrero | Electrical | Building 6 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2009 | 3 | 10500 | 2039
Mountain Empire | Potrero | Electrical | Building 7 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | No | 2016 | 3 | 10500 | 2046
Mountain Empire | Potrero | Electrical | Building 8 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | No | 2016 | 3 | 10500 | 2046
Mountain Empire | Potrero | Electrical | Building 9 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | No | 2016 | 3 | 10500 | 2046
Mountain Empire | Potrero | Electrical | Building 10 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1986 | 3 | 10500 | 2019 | 1 2019: 10500
Mountain Empire | Potrero | Electrical | Building 11 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2009 | 3 | 10500 | 2039
Mountain Empire | Potrero | Electrical | Computer Lab | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2003 | 3 | 10500 | 2033 | 15 2033: 14910
Mountain Empire | Potrero | Electrical | Speech Center | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1991 | 3 | 10500 | 2021 | 3 2021: 11130
Mountain Empire | Potrero | Electrical | Lower Restroom | Panel 100A 208/120 3P |  | 1 | 8500 | 30 | Yes | 2000 | 3 | 8500 | 2030 | 12 2030: 11305
Mountain Empire | Potrero | Electrical | Office | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2002 | 3 | 10500 | 2032 | 14 2032: 14595
Mountain Empire | Potrero | Paving | Kinder Blacktop | Asphalt Playground |  | 3359 | 5.5 | 30 | No | 1990 | 1 | 18474.5 | 2019 | 1 2019: 18474.5
Mountain Empire | Potrero | Paving | East Parking Lot | Asphalt Parking Lot |  | 5821 | 7.5 | 30 | No | 1990 | 1 | 43657.5 | 2019 | 1 2019: 43657.5
Mountain Empire | Potrero | Paving | Main Blacktop | Asphalt Playground |  | 14365 | 5.5 | 30 | No | 1990 | 1 | 79007.5 | 2019 | 1 2019: 79007.5
Mountain Empire | Potrero | Paving | Fire Lane | Asphalt Parking Lot |  | 2674 | 7.5 | 30 | No | 1990 | 1 | 20055 | 2019 | 1 2019: 20055
Mountain Empire | Potrero | Paving | Blacktop/Quad | Asphalt Playground |  | 7710 | 5.5 | 30 | No | 1990 | 2 | 42405 | 2019 | 1 2019: 42405
Mountain Empire | Potrero | Paving | Kinder Blacktop | Seal Coat and Stripe |  | 3359 | 0.35 | 5 | No | 2005 | 1 | 1175.65 | 2019 | 1 2019: 1175.65; 6 2024: 1351.9975; 11 2029: 1528.345; 16 2034: 1704.6925
Mountain Empire | Potrero | Paving | East Parking Lot | Seal Coat and Stripe |  | 5821 | 0.35 | 5 | No | 2005 | 1 | 2037.35 | 2019 | 1 2019: 2037.35; 6 2024: 2342.9525; 11 2029: 2648.555; 16 2034: 2954.1575
Mountain Empire | Potrero | Paving | Main Blacktop | Seal Coat and Stripe |  | 14365 | 0.35 | 5 | No | 2005 | 1 | 5027.75 | 2019 | 1 2019: 5027.75; 6 2024: 5781.9125; 11 2029: 6536.075; 16 2034: 7290.2375
Mountain Empire | Potrero | Paving | Fire Lane | Seal Coat and Stripe |  | 2674 | 0.35 | 5 | No | 2005 | 1 | 935.9 | 2019 | 1 2019: 935.9; 6 2024: 1076.285; 11 2029: 1216.67; 16 2034: 1357.055
Mountain Empire | Potrero | Paving | Blacktop/Quad | Seal Coat and Stripe |  | 7710 | 0.35 | 5 | No | 2005 | 1 | 2698.5 | 2019 | 1 2019: 2698.5; 6 2024: 3103.275; 11 2029: 3508.05; 16 2034: 3912.825
Mountain Empire | Potrero | Playground | Primary Playground 1 | Rubber Pour in Place |  | 1821 | 30 | 10 | No | 2012 | 3 | 54630 | 2022 | 4 2022: 59546.7; 14 2032: 75935.7
Mountain Empire | Potrero | Playground | Primary Playground 2 | Rubber Pour in Place |  | 826 | 30 | 10 | No | 2012 | 3 | 24780 | 2022 | 4 2022: 27010.2; 14 2032: 34444.2
Mountain Empire | Potrero | Playground | Kinder Playground | Rubber Pour in Place |  | 2015 | 30 | 10 | No | 2012 | 3 | 60450 | 2022 | 4 2022: 65890.5; 14 2032: 84025.5
Mountain Empire | Potrero | Fencing | Perimeter Fence | 2" Chain Link, Galv, 6' |  | 867 | 22.5 | 15 | No | 1995 | 3 | 19507.5 | 2019 | 1 2019: 19507.5; 16 2034: 28285.875
Mountain Empire | Potrero | Fencing | Parking Lot Fence | 2" Chain Link, Galv, 4' |  | 123 | 18.75 | 15 | No | 1995 | 3 | 2306.25 | 2019 | 1 2019: 2306.25; 16 2034: 3344.0625
Mountain Empire | Potrero | Fencing | Kinder Fence | 2" Chain Link, Galv, 6' |  | 87 | 22.5 | 15 | No | 1995 | 3 | 1957.5 | 2019 | 1 2019: 1957.5; 16 2034: 2838.375
Mountain Empire | Potrero | Fencing | Southeast Fence | 2" Chain Link, Galv, 4' |  | 196 | 18.75 | 15 | No | 1995 | 3 | 3675 | 2019 | 1 2019: 3675; 16 2034: 5328.75
Mountain Empire | Potrero | Fencing | Ball Field Fence | 2" Chain Link, Galv, 6' |  | 188 | 22.5 | 15 | No | 1995 | 3 | 4230 | 2019 | 1 2019: 4230; 16 2034: 6133.5
Mountain Empire | Potrero | Fencing | West Parking Lot Fence | 2" Chain Link, Galv, 4' |  | 121 | 18.75 | 15 | No | 1995 | 3 | 2268.75 | 2019 | 1 2019: 2268.75; 16 2034: 3289.6875
Mountain Empire | Potrero | Fencing | Well Fence | 2" Chain Link, Galv, 6' |  | 167 | 22.5 | 15 | No | 1995 | 3 | 3757.5 | 2019 | 1 2019: 3757.5; 16 2034: 5448.375
Mountain Empire | Potrero | Fencing | Playground 1 Fence | 2" Chain Link, Galv, 4' |  | 350 | 18.75 | 15 | No | 1995 | 3 | 6562.5 | 2019 | 1 2019: 6562.5; 16 2034: 9515.625
Mountain Empire | Potrero | Fencing | Preschool Fence | 2" Chain Link, Galv, 4' |  | 434 | 18.75 | 15 | No | 1995 | 3 | 8137.5 | 2019 | 1 2019: 8137.5; 16 2034: 11799.375
Mountain Empire | CloverFlat | Roofing | Office | BUR - Gran Cap |  | 2343 | 15 | 25 | Yes | 2000 | 3 | 35145 | 2025 | 7 2025: 41471.1
Mountain Empire | CloverFlat | Roofing | Building 1 | BUR - Gran Cap |  | 1070 | 15 | 25 | Yes | 2000 | 3 | 16050 | 2025 | 7 2025: 18939
Mountain Empire | CloverFlat | Roofing | Building 2 | Standing Seam |  | 1181 | 25 | 25 | Yes | 1990 | 3 | 29525 | 2019 | 1 2019: 29525
Mountain Empire | CloverFlat | Roofing | Building 3 | BUR - Gran Cap |  | 1110 | 15 | 25 | Yes | 1986 | 2 | 16650 | 2019 | 1 2019: 16650
Mountain Empire | CloverFlat | Roofing | Building 4 | BUR - Gran Cap |  | 1123 | 15 | 25 | Yes | 1986 | 2 | 16845 | 2019 | 1 2019: 16845
Mountain Empire | CloverFlat | Roofing | Building 7 | Standing Seam |  | 1078 | 25 | 25 | Yes | 2000 | 3 | 26950 | 2025 | 7 2025: 31801
Mountain Empire | CloverFlat | Roofing | Building 8 | BUR - Gran Cap |  | 1113 | 15 | 25 | Yes | 2000 | 2 | 16695 | 2020 | 2 2020: 17195.85
Mountain Empire | CloverFlat | Roofing | Building 9 | BUR - Gran Cap |  | 1112 | 15 | 25 | Yes | 2001 | 3 | 16680 | 2026 | 8 2026: 20182.8
Mountain Empire | CloverFlat | Roofing | Building 10 | BUR - Gran Cap |  | 1113 | 15 | 25 | Yes | 2001 | 3 | 16695 | 2026 | 8 2026: 20200.95
Mountain Empire | CloverFlat | Roofing | Building 12 | Standing Seam |  | 1060 | 25 | 25 | Yes | 2003 | 3 | 26500 | 2028 | 10 2028: 33655
Mountain Empire | CloverFlat | Roofing | Cafeteria | Poly Foam |  | 3462 | 10 | 10 | No | 2006 | 3 | 34620 | 2019 | 1 2019: 34620; 11 2029: 45006
Mountain Empire | CloverFlat | Roofing | Restroom | BUR - Gran Cap |  | 638 | 15 | 25 | Yes | 2000 | 3 | 9570 | 2025 | 7 2025: 11292.6
Mountain Empire | CloverFlat | Roofing | Headstart | BUR - Gran Cap |  | 1554 | 15 | 25 | Yes | 2000 | 2 | 23310 | 2020 | 2 2020: 24009.3
Mountain Empire | CloverFlat | Roofing | Shade Structure | Vinyl Fabric |  | 839 | 15 | 10 | No | 2013 | 3 | 12585 | 2023 | 5 2023: 14095.2; 15 2033: 17870.7
Mountain Empire | CloverFlat | Paving | AC Playground | Asphalt Playground |  | 22214 | 5.5 | 30 | No | 2015 | 3 | 122177 | 2045
Mountain Empire | CloverFlat | Paving | Campus Blacktop | Asphalt Playground |  | 10415 | 5.5 | 30 | No | 2015 | 3 | 57282.5 | 2045
Mountain Empire | CloverFlat | Paving | AC Playground | Seal Coat and Stripe |  | 22214 | 0.35 | 5 | No | 2015 | 3 | 7774.9 | 2020 | 2 2020: 8008.147; 7 2025: 9174.382; 12 2030: 10340.617; 17 2035: 11506.852
Mountain Empire | CloverFlat | Paving | Campus Blacktop | Seal Coat and Stripe |  | 10415 | 0.35 | 5 | No | 2015 | 3 | 3645.25 | 2020 | 2 2020: 3754.6075; 7 2025: 4301.395; 12 2030: 4848.1825; 17 2035: 5394.97
Mountain Empire | CloverFlat | HVAC | Restroom | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 2 | 12000 | 2021 | 3 2021: 12720; 18 2036: 18120
Mountain Empire | CloverFlat | HVAC | Building 7 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | CloverFlat | HVAC | Building 8 | Heat Pump |  | 1 | 12000 | 15 | Yes | 1990 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | CloverFlat | HVAC | Building 9 | Heat Pump |  | 1 | 12000 | 15 | Yes | 1990 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | CloverFlat | HVAC | Building 10 | Heat Pump |  | 1 | 12000 | 15 | Yes | 1990 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | CloverFlat | HVAC | Building 4 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | CloverFlat | HVAC | Building 3 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | CloverFlat | HVAC | Building 2 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | CloverFlat | HVAC | Building 1 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | CloverFlat | HVAC | Building 1 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | CloverFlat | HVAC | Headstart | Heat Pump |  | 1 | 12000 | 15 | Yes | 1990 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | CloverFlat | HVAC | Office | Heat Pump |  | 1 | 12000 | 15 | Yes | 1990 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | CloverFlat | HVAC | Office | Heat Pump |  | 1 | 12000 | 15 | Yes | 1990 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | CloverFlat | HVAC | Building 12 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | CloverFlat | HVAC | Cafeteria | Heat Pump |  | 1 | 12000 | 15 | No | 1990 | 3 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | CloverFlat | HVAC | Cafeteria | Heat Pump |  | 1 | 12000 | 15 | No | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | CloverFlat | HVAC | Cafeteria | Heat Pump |  | 1 | 12000 | 15 | No | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | CloverFlat | HVAC | Cafeteria | Heat Pump |  | 1 | 12000 | 15 | No | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | CloverFlat | HVAC | Cafeteria | Heat Pump |  | 1 | 12000 | 15 | No | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | CloverFlat | Electrical | Office | Fluorescent CR Lighting |  | 1920 | 4 | 20 | Yes | 2000 | 3 | 7680 | 2020 | 2 2020: 7910.4
Mountain Empire | CloverFlat | Electrical | Building 1 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2000 | 3 | 3840 | 2020 | 2 2020: 3955.2
Mountain Empire | CloverFlat | Electrical | Building 2 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1990 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | CloverFlat | Electrical | Building 3 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1986 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | CloverFlat | Electrical | Building 4 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 1986 | 3 | 3840 | 2019 | 1 2019: 3840
Mountain Empire | CloverFlat | Electrical | Building 7 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2000 | 3 | 3840 | 2020 | 2 2020: 3955.2
Mountain Empire | CloverFlat | Electrical | Building 8 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2000 | 3 | 3840 | 2020 | 2 2020: 3955.2
Mountain Empire | CloverFlat | Electrical | Building 9 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2001 | 3 | 3840 | 2021 | 3 2021: 4070.4
Mountain Empire | CloverFlat | Electrical | Building 10 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2001 | 3 | 3840 | 2021 | 3 2021: 4070.4
Mountain Empire | CloverFlat | Electrical | Building 12 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2003 | 3 | 3840 | 2023 | 5 2023: 4300.8
Mountain Empire | CloverFlat | Electrical | Cafeteria | Fluorescent CR Lighting |  | 2560 | 4 | 20 | No | 1980 | 3 | 10240 | 2019 | 1 2019: 10240
Mountain Empire | CloverFlat | Electrical | Restroom | Fluorescent CR Lighting |  | 480 | 4 | 20 | Yes | 2000 | 3 | 1920 | 2020 | 2 2020: 1977.6
Mountain Empire | CloverFlat | Electrical | Headstart | Fluorescent CR Lighting |  | 1440 | 4 | 20 | Yes | 2000 | 3 | 5760 | 2020 | 2 2020: 5932.8
Mountain Empire | CloverFlat | Electrical | Office | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | CloverFlat | Electrical | Building 1 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | CloverFlat | Electrical | Building 2 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1990 | 3 | 10500 | 2020 | 2 2020: 10815
Mountain Empire | CloverFlat | Electrical | Building 3 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1986 | 3 | 10500 | 2019 | 1 2019: 10500
Mountain Empire | CloverFlat | Electrical | Building 4 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 1986 | 3 | 10500 | 2019 | 1 2019: 10500
Mountain Empire | CloverFlat | Electrical | Building 7 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | CloverFlat | Electrical | Building 8 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | CloverFlat | Electrical | Building 9 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2001 | 3 | 10500 | 2031 | 13 2031: 14280
Mountain Empire | CloverFlat | Electrical | Building 10 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2001 | 3 | 10500 | 2031 | 13 2031: 14280
Mountain Empire | CloverFlat | Electrical | Building 12 | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2003 | 3 | 10500 | 2033 | 15 2033: 14910
Mountain Empire | CloverFlat | Electrical | Cafeteria | Panel 200A 208/120 3P |  | 2 | 10500 | 30 | No | 1980 | 3 | 21000 | 2019 | 1 2019: 21000
Mountain Empire | CloverFlat | Electrical | Restroom | Panel 100A 208/120 3P |  | 1 | 8500 | 30 | Yes | 2000 | 3 | 8500 | 2030 | 12 2030: 11305
Mountain Empire | CloverFlat | Electrical | Headstart | Panel 200A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | CloverFlat | Plumbing | Office | DCW/Sewer |  | 1920 | 18 | 30 | Yes | 2000 | 3 | 34560 | 2030 | 12 2030: 45964.8
Mountain Empire | CloverFlat | Plumbing | Building 1 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2000 | 3 | 17280 | 2030 | 12 2030: 22982.4
Mountain Empire | CloverFlat | Plumbing | Building 2 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1990 | 3 | 17280 | 2020 | 2 2020: 17798.4
Mountain Empire | CloverFlat | Plumbing | Building 3 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1986 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | CloverFlat | Plumbing | Building 4 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 1986 | 3 | 17280 | 2019 | 1 2019: 17280
Mountain Empire | CloverFlat | Plumbing | Building 7 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2000 | 3 | 17280 | 2030 | 12 2030: 22982.4
Mountain Empire | CloverFlat | Plumbing | Building 8 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2000 | 3 | 17280 | 2030 | 12 2030: 22982.4
Mountain Empire | CloverFlat | Plumbing | Building 9 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2001 | 3 | 17280 | 2031 | 13 2031: 23500.8
Mountain Empire | CloverFlat | Plumbing | Building 10 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2001 | 3 | 17280 | 2031 | 13 2031: 23500.8
Mountain Empire | CloverFlat | Plumbing | Building 12 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2003 | 3 | 17280 | 2033 | 15 2033: 24537.6
Mountain Empire | CloverFlat | Plumbing | Cafeteria | DCW/Sewer |  | 2560 | 18 | 30 | No | 1980 | 3 | 46080 | 2019 | 1 2019: 46080
Mountain Empire | CloverFlat | Plumbing | Restroom | DCW/Sewer |  | 480 | 18 | 30 | Yes | 2000 | 3 | 8640 | 2030 | 12 2030: 11491.2
Mountain Empire | CloverFlat | Plumbing | Headstart | DCW/Sewer |  | 1440 | 18 | 30 | Yes | 2000 | 3 | 25920 | 2030 | 12 2030: 34473.6
Mountain Empire | CloverFlat | Finishes | Office | Carpet Roll |  | 1920 | 7.9 | 15 | Yes | 2000 | 3 | 15168 | 2019 | 1 2019: 15168; 16 2034: 21993.6
Mountain Empire | CloverFlat | Finishes | Building 1 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2000 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | CloverFlat | Finishes | Building 2 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1990 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | CloverFlat | Finishes | Building 3 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1986 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | CloverFlat | Finishes | Building 4 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 1986 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | CloverFlat | Finishes | Building 7 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2000 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | CloverFlat | Finishes | Building 8 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2000 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | CloverFlat | Finishes | Building 9 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2001 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | CloverFlat | Finishes | Building 10 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2001 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | CloverFlat | Finishes | Building 12 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2003 | 3 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | CloverFlat | Finishes | Cafeteria | Carpet Roll |  | 2560 | 7.9 | 15 | No | 1980 | 3 | 20224 | 2019 | 1 2019: 20224; 16 2034: 29324.8
Mountain Empire | CloverFlat | Finishes | Restroom | Vinyl Sheet |  | 480 | 9.75 | 12 | Yes | 2000 | 3 | 4680 | 2019 | 1 2019: 4680; 13 2031: 6364.8
Mountain Empire | CloverFlat | Finishes | Headstart | Carpet Roll |  | 1440 | 7.9 | 15 | Yes | 2000 | 3 | 11376 | 2019 | 1 2019: 11376; 16 2034: 16495.2
Mountain Empire | CloverFlat | Finishes | Office | Paint Exterior |  | 1920 | 1.6 | 10 | Yes | 2014 | 3 | 3072 | 2024 | 6 2024: 3532.8; 16 2034: 4454.4
Mountain Empire | CloverFlat | Finishes | Building 1 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | CloverFlat | Finishes | Building 2 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | CloverFlat | Finishes | Building 3 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | CloverFlat | Finishes | Building 4 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | CloverFlat | Finishes | Building 7 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | CloverFlat | Finishes | Building 8 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | CloverFlat | Finishes | Building 9 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | CloverFlat | Finishes | Building 10 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | CloverFlat | Finishes | Building 12 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2014 | 3 | 1536 | 2024 | 6 2024: 1766.4; 16 2034: 2227.2
Mountain Empire | CloverFlat | Finishes | Cafeteria | Paint Exterior |  | 2560 | 1.6 | 10 | No | 2014 | 3 | 4096 | 2024 | 6 2024: 4710.4; 16 2034: 5939.2
Mountain Empire | CloverFlat | Finishes | Restroom | Paint Exterior |  | 480 | 1.6 | 10 | Yes | 2014 | 3 | 768 | 2024 | 6 2024: 883.2; 16 2034: 1113.6
Mountain Empire | CloverFlat | Finishes | Headstart | Paint Exterior |  | 1440 | 1.6 | 10 | Yes | 2014 | 3 | 2304 | 2024 | 6 2024: 2649.6; 16 2034: 3340.8
Mountain Empire | CloverFlat | Finishes | Office | Paint Interior |  | 1920 | 1.5 | 10 | Yes | 2000 | 3 | 2880 | 2019 | 1 2019: 2880; 11 2029: 3744
Mountain Empire | CloverFlat | Finishes | Building 1 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2000 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | CloverFlat | Finishes | Building 2 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1990 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | CloverFlat | Finishes | Building 3 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1986 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | CloverFlat | Finishes | Building 4 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 1986 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | CloverFlat | Finishes | Building 7 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2000 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | CloverFlat | Finishes | Building 8 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2000 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | CloverFlat | Finishes | Building 9 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2001 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | CloverFlat | Finishes | Building 10 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2001 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | CloverFlat | Finishes | Building 12 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2003 | 3 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | CloverFlat | Finishes | Cafeteria | Paint Interior |  | 2560 | 1.5 | 10 | No | 1980 | 3 | 3840 | 2019 | 1 2019: 3840; 11 2029: 4992
Mountain Empire | CloverFlat | Finishes | Restroom | Paint Interior |  | 480 | 1.5 | 10 | Yes | 2000 | 3 | 720 | 2019 | 1 2019: 720; 11 2029: 936
Mountain Empire | CloverFlat | Finishes | Headstart | Paint Interior |  | 1440 | 1.5 | 10 | Yes | 2000 | 3 | 2160 | 2019 | 1 2019: 2160; 11 2029: 2808
Mountain Empire | CloverFlat | LowVoltage |  | FACP |  | 1 | 20000 | 15 | Yes | 2000 | 3 | 20000 | 2019 | 1 2019: 20000; 16 2034: 29000
Mountain Empire | CloverFlat | LowVoltage |  | Clock/Bell/Paging |  | 1 | 40000 | 20 | Yes | 2000 | 3 | 40000 | 2020 | 2 2020: 41200
Mountain Empire | CloverFlat | Playground |  | Wood Fiber |  | 9419 | 3.15 | 5 | No | 2003 | 3 | 29669.85 | 2019 | 1 2019: 29669.85; 6 2024: 34120.3275; 11 2029: 38570.805; 16 2034: 43021.2825
Mountain Empire | CloverFlat | Fencing | Perimeter Fence | 2" Chain Link, Galv, 6' |  | 1869 | 22.5 | 15 | No | 1980 | 3 | 42052.5 | 2019 | 1 2019: 42052.5; 16 2034: 60976.125
Mountain Empire | CloverFlat | Fencing | Admin Fence | 2" Chain Link, Galv, 4' |  | 225 | 18.75 | 15 | No | 2000 | 3 | 4218.75 | 2019 | 1 2019: 4218.75; 16 2034: 6117.1875
Mountain Empire | CloverFlat | Fencing | Pedestrian Fence | 2" Chain Link, Galv, 4' |  | 275 | 18.75 | 15 | No | 2000 | 3 | 5156.25 | 2019 | 1 2019: 5156.25; 16 2034: 7476.5625
Mountain Empire | CloverFlat | Fencing | Parking Lot Fence | 2" Chain Link, Galv, 4' |  | 116 | 18.75 | 15 | No | 2000 | 3 | 2175 | 2019 | 1 2019: 2175; 16 2034: 3153.75
Mountain Empire | CloverFlat | Fencing | Headstart Fence | 2" Chain Link, Galv, 4' |  | 311 | 18.75 | 15 | No | 2000 | 3 | 5831.25 | 2019 | 1 2019: 5831.25; 16 2034: 8455.3125
Mountain Empire | CloverFlat | Fencing | Solar Fence | 2" Chain Link, Galv, 6' |  | 228 | 22.5 | 15 | No | 2012 | 3 | 5130 | 2027 | 9 2027: 6361.2
Mountain Empire | Descanso | Roofing | Admin | Ashpalt Shingle | Admin | 3933 | 9.5 | 15 | No | 1980 | 3 | 37363.5 | 2019 | 1 2019: 37363.5; 16 2034: 54177.075
Mountain Empire | Descanso | Roofing | Building 1 | Ashpalt Shingle | 1 | 3291 | 9.5 | 15 | No | 1980 | 3 | 31264.5 | 2019 | 1 2019: 31264.5; 16 2034: 45333.525
Mountain Empire | Descanso | Roofing | Building 1 | Ashpalt Shingle | 1A | 309 | 9.5 | 15 | No | 1980 | 3 | 2935.5 | 2019 | 1 2019: 2935.5; 16 2034: 4256.475
Mountain Empire | Descanso | Roofing | Building 1 | BUR - Gran Cap | 1B | 501 | 15 | 25 | No | 1980 | 3 | 7515 | 2019 | 1 2019: 7515
Mountain Empire | Descanso | Roofing | Building 2 | Ashpalt Shingle | 2 | 1869 | 9.5 | 15 | No | 1980 | 3 | 17755.5 | 2019 | 1 2019: 17755.5; 16 2034: 25745.475
Mountain Empire | Descanso | Roofing | Building 2 | BUR - Gran Cap | 2A | 658 | 15 | 25 | No | 1980 | 1 | 9870 | 2019 | 1 2019: 9870
Mountain Empire | Descanso | Roofing | Room 7 | BUR - Gran Cap |  | 1176 | 15 | 25 | Yes | 2016 | 3 | 17640 | 2041
Mountain Empire | Descanso | Roofing | Room 8 | BUR - Gran Cap |  | 1133 | 15 | 25 | Yes | 2016 | 3 | 16995 | 2041
Mountain Empire | Descanso | Roofing | Room 9 | BUR - Gran Cap |  | 1257 | 15 | 25 | Yes | 2000 | 3 | 18855 | 2025 | 7 2025: 22248.9
Mountain Empire | Descanso | Roofing | Room 10 | BUR - Gran Cap |  | 1300 | 15 | 25 | Yes | 2000 | 3 | 19500 | 2025 | 7 2025: 23010
Mountain Empire | Descanso | Roofing | ASP | Standing Seam |  | 2361 | 25 | 25 | Yes | 2003 | 3 | 59025 | 2028 | 10 2028: 74961.75
Mountain Empire | Descanso | Roofing | Restroom | Standing Seam |  | 596 | 25 | 25 | Yes | 2003 | 3 | 14900 | 2028 | 10 2028: 18923
Mountain Empire | Descanso | Paving | Parking Lot | Asphalt Parking Lot |  | 15261 | 7.5 | 30 | No | 1980 | 1 | 114457.5 | 2019 | 1 2019: 114457.5
Mountain Empire | Descanso | Paving | Kinder Blacktop | Asphalt Playground |  | 1373 | 5.5 | 30 | No | 1980 | 3 | 7551.5 | 2019 | 1 2019: 7551.5
Mountain Empire | Descanso | Paving | Blacktop | Asphalt Playground |  | 20808 | 5.5 | 30 | No | 2015 | 3 | 114444 | 2045
Mountain Empire | Descanso | Paving | Quad | Asphalt Playground |  | 2646 | 5.5 | 30 | No | 1980 | 1 | 14553 | 2019 | 1 2019: 14553
Mountain Empire | Descanso | Paving | Parking Lot | Seal Coat and Stripe |  | 15261 | 0.35 | 5 | No | 2010 | 3 | 5341.35 | 2019 | 1 2019: 5341.35; 6 2024: 6142.5525; 11 2029: 6943.755; 16 2034: 7744.9575
Mountain Empire | Descanso | Paving | Kinder Blacktop | Seal Coat and Stripe |  | 1373 | 0.35 | 5 | No | 2010 | 1 | 480.55 | 2019 | 1 2019: 480.55; 6 2024: 552.6325; 11 2029: 624.715; 16 2034: 696.7975
Mountain Empire | Descanso | Paving | Blacktop | Seal Coat and Stripe |  | 20808 | 0.35 | 5 | No | 2015 | 3 | 7282.8 | 2020 | 2 2020: 7501.284; 7 2025: 8593.704; 12 2030: 9686.124; 17 2035: 10778.544
Mountain Empire | Descanso | Paving | Quad | Seal Coat and Stripe |  | 2646 | 0.35 | 5 | No | 2010 | 1 | 926.1 | 2019 | 1 2019: 926.1; 6 2024: 1065.015; 11 2029: 1203.93; 16 2034: 1342.845
Mountain Empire | Descanso | Fencing | SE Fence | 2" Chain Link, Galv, 4' |  | 229 | 18.75 | 15 | No | 2005 | 3 | 4293.75 | 2020 | 2 2020: 4422.5625; 17 2035: 6354.75
Mountain Empire | Descanso | Fencing | SW Fence | 2" Chain Link, Galv, 4' |  | 147 | 18.75 | 15 | No | 2005 | 3 | 2756.25 | 2020 | 2 2020: 2838.9375; 17 2035: 4079.25
Mountain Empire | Descanso | Fencing | Perimeter Fence | 2" Chain Link, Galv, 6' |  | 1305 | 22.5 | 15 | No | 2005 | 3 | 29362.5 | 2020 | 2 2020: 30243.375; 17 2035: 43456.5
Mountain Empire | Descanso | LowVoltage |  | FACP |  | 1 | 20000 | 15 | No | 2000 | 3 | 20000 | 2019 | 1 2019: 20000; 16 2034: 29000
Mountain Empire | Descanso | LowVoltage |  | Clock/Bell/Paging |  | 1 | 40000 | 20 | No | 2000 | 3 | 40000 | 2020 | 2 2020: 41200
Mountain Empire | Descanso | Playground |  | Wood Fiber |  | 9100 | 3.15 | 5 | No | 2003 | 3 | 28665 | 2019 | 1 2019: 28665; 6 2024: 32964.75; 11 2029: 37264.5; 16 2034: 41564.25
Mountain Empire | Descanso | Finishes | Admin | Carpet Roll |  | 3289 | 7.9 | 15 | No | 2000 | 2 | 25983.1 | 2019 | 1 2019: 25983.1; 16 2034: 37675.495
Mountain Empire | Descanso | Finishes | Building 1 | Carpet Roll |  | 3724 | 7.9 | 15 | No | 2000 | 2 | 29419.6 | 2019 | 1 2019: 29419.6; 16 2034: 42658.42
Mountain Empire | Descanso | Finishes | Building 2 | Carpet Roll |  | 1596 | 7.9 | 15 | No | 2000 | 2 | 12608.4 | 2019 | 1 2019: 12608.4; 16 2034: 18282.18
Mountain Empire | Descanso | Finishes | Room 7 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2016 | 3 | 7584 | 2031 | 13 2031: 10314.24
Mountain Empire | Descanso | Finishes | Room 8 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2016 | 3 | 7584 | 2031 | 13 2031: 10314.24
Mountain Empire | Descanso | Finishes | Room 9 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2000 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Descanso | Finishes | Room 10 | Carpet Roll |  | 960 | 7.9 | 15 | Yes | 2000 | 2 | 7584 | 2019 | 1 2019: 7584; 16 2034: 10996.8
Mountain Empire | Descanso | Finishes | ASP | Carpet Roll |  | 1920 | 7.9 | 15 | Yes | 2003 | 2 | 15168 | 2019 | 1 2019: 15168; 16 2034: 21993.6
Mountain Empire | Descanso | Finishes | Restroom | Vinyl Sheet |  | 480 | 9.75 | 12 | Yes | 2003 | 2 | 4680 | 2019 | 1 2019: 4680; 13 2031: 6364.8
Mountain Empire | Descanso | Finishes | Admin | Paint Exterior |  | 3289 | 1.6 | 10 | No | 2000 | 2 | 5262.4 | 2019 | 1 2019: 5262.4; 11 2029: 6841.12
Mountain Empire | Descanso | Finishes | Building 1 | Paint Exterior |  | 3724 | 1.6 | 10 | No | 2000 | 2 | 5958.4 | 2019 | 1 2019: 5958.4; 11 2029: 7745.92
Mountain Empire | Descanso | Finishes | Building 2 | Paint Exterior |  | 1596 | 1.6 | 10 | No | 2000 | 2 | 2553.6 | 2019 | 1 2019: 2553.6; 11 2029: 3319.68
Mountain Empire | Descanso | Finishes | Room 7 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2016 | 3 | 1536 | 2026 | 8 2026: 1858.56; 18 2036: 2319.36
Mountain Empire | Descanso | Finishes | Room 8 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2016 | 3 | 1536 | 2026 | 8 2026: 1858.56; 18 2036: 2319.36
Mountain Empire | Descanso | Finishes | Room 9 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2000 | 2 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | Descanso | Finishes | Room 10 | Paint Exterior |  | 960 | 1.6 | 10 | Yes | 2000 | 2 | 1536 | 2019 | 1 2019: 1536; 11 2029: 1996.8
Mountain Empire | Descanso | Finishes | ASP | Paint Exterior |  | 1920 | 1.6 | 10 | Yes | 2003 | 2 | 3072 | 2019 | 1 2019: 3072; 11 2029: 3993.6
Mountain Empire | Descanso | Finishes | Restroom | Paint Exterior |  | 480 | 1.6 | 10 | Yes | 2003 | 2 | 768 | 2019 | 1 2019: 768; 11 2029: 998.4
Mountain Empire | Descanso | Finishes | Admin | Paint Interior |  | 3289 | 1.5 | 10 | No | 2000 | 2 | 4933.5 | 2019 | 1 2019: 4933.5; 11 2029: 6413.55
Mountain Empire | Descanso | Finishes | Building 1 | Paint Interior |  | 3724 | 1.5 | 10 | No | 2000 | 2 | 5586 | 2019 | 1 2019: 5586; 11 2029: 7261.8
Mountain Empire | Descanso | Finishes | Building 2 | Paint Interior |  | 1596 | 1.5 | 10 | No | 2000 | 2 | 2394 | 2019 | 1 2019: 2394; 11 2029: 3112.2
Mountain Empire | Descanso | Finishes | Room 7 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2016 | 3 | 1440 | 2026 | 8 2026: 1742.4; 18 2036: 2174.4
Mountain Empire | Descanso | Finishes | Room 8 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2016 | 3 | 1440 | 2026 | 8 2026: 1742.4; 18 2036: 2174.4
Mountain Empire | Descanso | Finishes | Room 9 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2000 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Descanso | Finishes | Room 10 | Paint Interior |  | 960 | 1.5 | 10 | Yes | 2000 | 2 | 1440 | 2019 | 1 2019: 1440; 11 2029: 1872
Mountain Empire | Descanso | Finishes | ASP | Paint Interior |  | 1920 | 1.5 | 10 | Yes | 2003 | 2 | 2880 | 2019 | 1 2019: 2880; 11 2029: 3744
Mountain Empire | Descanso | Finishes | Restroom | Paint Interior |  | 480 | 1.5 | 10 | Yes | 2003 | 2 | 720 | 2019 | 1 2019: 720; 11 2029: 936
Mountain Empire | Descanso | Electrical | Admin | Fluorescent CR Lighting |  | 3289 | 4 | 20 | No | 2000 | 3 | 13156 | 2020 | 2 2020: 13550.68
Mountain Empire | Descanso | Electrical | Building 1 | Fluorescent CR Lighting |  | 3724 | 4 | 20 | No | 2000 | 3 | 14896 | 2020 | 2 2020: 15342.88
Mountain Empire | Descanso | Electrical | Building 2 | Fluorescent CR Lighting |  | 1596 | 4 | 20 | No | 2000 | 3 | 6384 | 2020 | 2 2020: 6575.52
Mountain Empire | Descanso | Electrical | Room 7 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2016 | 3 | 3840 | 2036 | 18 2036: 5798.4
Mountain Empire | Descanso | Electrical | Room 8 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2016 | 3 | 3840 | 2036 | 18 2036: 5798.4
Mountain Empire | Descanso | Electrical | Room 9 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2000 | 3 | 3840 | 2020 | 2 2020: 3955.2
Mountain Empire | Descanso | Electrical | Room 10 | Fluorescent CR Lighting |  | 960 | 4 | 20 | Yes | 2000 | 3 | 3840 | 2020 | 2 2020: 3955.2
Mountain Empire | Descanso | Electrical | ASP | Fluorescent CR Lighting |  | 1920 | 4 | 20 | Yes | 2003 | 3 | 7680 | 2023 | 5 2023: 8601.6
Mountain Empire | Descanso | Electrical | Restroom | Fluorescent CR Lighting |  | 480 | 4 | 20 | Yes | 2003 | 3 | 1920 | 2023 | 5 2023: 2150.4
Mountain Empire | Descanso | Plumbing | Admin | DCW/Sewer |  | 3289 | 18 | 30 | No | 1935 | 3 | 59202 | 2019 | 1 2019: 59202
Mountain Empire | Descanso | Plumbing | Building 1 | DCW/Sewer |  | 3724 | 18 | 30 | No | 1950 | 3 | 67032 | 2019 | 1 2019: 67032
Mountain Empire | Descanso | Plumbing | Building 2 | DCW/Sewer |  | 1596 | 18 | 30 | No | 1947 | 3 | 28728 | 2019 | 1 2019: 28728
Mountain Empire | Descanso | Plumbing | Room 7 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2016 | 3 | 17280 | 2046
Mountain Empire | Descanso | Plumbing | Room 8 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2016 | 3 | 17280 | 2046
Mountain Empire | Descanso | Plumbing | Room 9 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2000 | 3 | 17280 | 2030 | 12 2030: 22982.4
Mountain Empire | Descanso | Plumbing | Room 10 | DCW/Sewer |  | 960 | 18 | 30 | Yes | 2000 | 3 | 17280 | 2030 | 12 2030: 22982.4
Mountain Empire | Descanso | Plumbing | ASP | DCW/Sewer |  | 1920 | 18 | 30 | Yes | 2003 | 3 | 34560 | 2033 | 15 2033: 49075.2
Mountain Empire | Descanso | Plumbing | Restroom | DCW/Sewer |  | 480 | 18 | 30 | Yes | 2003 | 3 | 8640 | 2033 | 15 2033: 12268.8
Mountain Empire | Descanso | HVAC | Room 7 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2016 | 3 | 12000 | 2031 | 13 2031: 16320
Mountain Empire | Descanso | HVAC | Room 8 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2016 | 3 | 12000 | 2031 | 13 2031: 16320
Mountain Empire | Descanso | HVAC | ASP | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Descanso | HVAC | ASP | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Descanso | HVAC | Room 9 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Descanso | HVAC | Room 9 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Descanso | HVAC | Room 10 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Descanso | HVAC | Room 10 | Heat Pump |  | 1 | 12000 | 15 | Yes | 2009 | 3 | 12000 | 2024 | 6 2024: 13800
Mountain Empire | Descanso | HVAC | Building 2 | Package Unit 4 Ton |  | 1 | 10000 | 15 | No | 1980 | 3 | 10000 | 2019 | 1 2019: 10000; 16 2034: 14500
Mountain Empire | Descanso | HVAC | Building 2 | Package Unit 4 Ton |  | 1 | 10000 | 15 | No | 1980 | 3 | 10000 | 2019 | 1 2019: 10000; 16 2034: 14500
Mountain Empire | Descanso | HVAC | Building 2 | Package Unit 4 Ton |  | 1 | 10000 | 15 | No | 1980 | 3 | 10000 | 2019 | 1 2019: 10000; 16 2034: 14500
Mountain Empire | Descanso | HVAC | Building 2 | Package Unit 4 Ton |  | 1 | 10000 | 15 | No | 1980 | 3 | 10000 | 2019 | 1 2019: 10000; 16 2034: 14500
Mountain Empire | Descanso | HVAC | Building 2 | Package Unit 3.5 Ton |  | 1 | 8750 | 15 | No | 1980 | 3 | 8750 | 2019 | 1 2019: 8750; 16 2034: 12687.5
Mountain Empire | Descanso | HVAC | Building 1 | Package Unit 3 Ton |  | 1 | 7500 | 15 | No | 1980 | 3 | 7500 | 2019 | 1 2019: 7500; 16 2034: 10875
Mountain Empire | Descanso | HVAC | Building 1 | Package Unit 3 Ton |  | 1 | 7500 | 15 | No | 1980 | 3 | 7500 | 2019 | 1 2019: 7500; 16 2034: 10875
Mountain Empire | Descanso | Electrical | Admin | Panel 225A 208/120 3P |  | 1 | 10500 | 30 | No | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | Descanso | Electrical | Building 1 | Panel 225A 208/120 3P |  | 1 | 10500 | 30 | No | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | Descanso | Electrical | Building 2 | Panel 225A 208/120 3P |  | 1 | 10500 | 30 | No | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | Descanso | Electrical | Room 7 | Panel 225A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2016 | 3 | 10500 | 2046
Mountain Empire | Descanso | Electrical | Room 8 | Panel 225A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2016 | 3 | 10500 | 2046
Mountain Empire | Descanso | Electrical | Room 9 | Panel 225A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | Descanso | Electrical | Room 10 | Panel 225A 208/120 3P |  | 1 | 10500 | 30 | Yes | 2000 | 3 | 10500 | 2030 | 12 2030: 13965
Mountain Empire | Descanso | Electrical | ASP | Panel 225A 208/120 3P |  | 2 | 10500 | 30 | Yes | 2003 | 3 | 21000 | 2033 | 15 2033: 29820
Mountain Empire | Descanso | Electrical | Restroom | Panel 100A 208/120 3P |  | 1 | 8500 | 30 | Yes | 2003 | 3 | 8500 | 2033 | 15 2033: 12070
Mountain Empire | Descanso | Roofing | Building 1 | BUR - Gran Cap | 1C | 974 | 15 | 25 | Yes | 2013 | 2 | 14610 | 2033 | 15 2033: 20746.2
Mountain Empire | MountainEmpireAltEd | Roofing | Campo High | BUR - Gran Cap |  | 2295 | 15 | 25 | Yes | 2000 | 2 | 34425 | 2020 | 2 2020: 35457.75
Mountain Empire | MountainEmpireAltEd | Roofing | Office | Ashpalt Shingle |  | 2259 | 9.5 | 15 | No | 1990 | 1 | 21460.5 | 2019 | 1 2019: 21460.5; 16 2034: 31117.725
Mountain Empire | MountainEmpireAltEd | Roofing | Book Room | Ashpalt Shingle |  | 2363 | 9.5 | 15 | No | 1990 | 1 | 22448.5 | 2019 | 1 2019: 22448.5; 16 2034: 32550.325
Mountain Empire | MountainEmpireAltEd | Roofing | Restroom | BUR - Gran Cap |  | 485 | 15 | 25 | Yes | 2000 | 1 | 7275 | 2019 | 1 2019: 7275
Mountain Empire | MountainEmpireAltEd | Paving | North Parking Lot | Asphalt Parking Lot |  | 9874 | 7.5 | 30 | No | 1980 | 1 | 74055 | 2019 | 1 2019: 74055
Mountain Empire | MountainEmpireAltEd | Paving | Blacktop | Asphalt Playground |  | 2074 | 5.5 | 30 | No | 1980 | 1 | 11407 | 2019 | 1 2019: 11407
Mountain Empire | MountainEmpireAltEd | Paving | North Parking Lot | Seal Coat and Stripe |  | 9874 | 0.35 | 5 | No | 1980 | 1 | 3455.9 | 2019 | 1 2019: 3455.9; 6 2024: 3974.285; 11 2029: 4492.67; 16 2034: 5011.055
Mountain Empire | MountainEmpireAltEd | Paving | Blacktop | Seal Coat and Stripe |  | 2074 | 0.35 | 5 | No | 1980 | 1 | 725.9 | 2019 | 1 2019: 725.9; 6 2024: 834.785; 11 2029: 943.67; 16 2034: 1052.555
Mountain Empire | MountainEmpireAltEd | HVAC | Campo High | Heat Pump |  | 1 | 12000 | 15 | Yes | 2000 | 2 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireAltEd | HVAC | Campo High | Heat Pump |  | 1 | 12000 | 15 | Yes | 2000 | 2 | 12000 | 2019 | 1 2019: 12000; 16 2034: 17400
Mountain Empire | MountainEmpireAltEd | LowVoltage |  | FACP |  | 1 | 20000 | 15 | No | 2000 | 3 | 20000 | 2019 | 1 2019: 20000; 16 2034: 29000
Mountain Empire | MountainEmpireAltEd | Finishes | Campo High | Paint Exterior |  | 1920 | 1.6 | 10 | Yes | 2015 | 3 | 3072 | 2025 | 7 2025: 3624.96; 17 2035: 4546.56
Mountain Empire | MountainEmpireAltEd | Finishes | Office | Paint Exterior |  | 2000 | 1.6 | 10 | No | 2015 | 3 | 3200 | 2025 | 7 2025: 3776; 17 2035: 4736
Mountain Empire | MountainEmpireAltEd | Finishes | Book Room | Paint Exterior |  | 2000 | 1.6 | 10 | No | 2015 | 3 | 3200 | 2025 | 7 2025: 3776; 17 2035: 4736
Mountain Empire | MountainEmpireAltEd | Finishes | Restroom | Paint Exterior |  | 460 | 1.6 | 10 | Yes | 2015 | 3 | 736 | 2025 | 7 2025: 868.48; 17 2035: 1089.28
Mountain Empire | MountainEmpireAltEd | Finishes | Campo High | Paint Interior |  | 1920 | 1.5 | 10 | Yes | 2000 | 2 | 2880 | 2019 | 1 2019: 2880; 11 2029: 3744
Mountain Empire | MountainEmpireAltEd | Finishes | Office | Paint Interior |  | 2000 | 1.5 | 10 | No | 1985 | 2 | 3000 | 2019 | 1 2019: 3000; 11 2029: 3900
Mountain Empire | MountainEmpireAltEd | Finishes | Book Room | Paint Interior |  | 2000 | 1.5 | 10 | No | 1985 | 2 | 3000 | 2019 | 1 2019: 3000; 11 2029: 3900
Mountain Empire | MountainEmpireAltEd | Finishes | Restroom | Paint Interior |  | 460 | 1.5 | 10 | Yes | 2000 | 2 | 690 | 2019 | 1 2019: 690; 11 2029: 897
Mountain Empire | MountainEmpireAltEd | Finishes | Campo High | Carpet Roll |  | 1920 | 7.9 | 15 | Yes | 2000 | 2 | 15168 | 2019 | 1 2019: 15168; 16 2034: 21993.6
Mountain Empire | MountainEmpireAltEd | Finishes | Office | Carpet Roll |  | 2000 | 7.9 | 15 | No | 2015 | 3 | 15800 | 2030 | 12 2030: 21014
Mountain Empire | MountainEmpireAltEd | Finishes | Book Room | Carpet Roll |  | 2000 | 7.9 | 15 | No | 1995 | 2 | 15800 | 2019 | 1 2019: 15800; 16 2034: 22910
Mountain Empire | MountainEmpireAltEd | Finishes | Restroom | Vinyl Sheet |  | 460 | 9.75 | 12 | Yes | 2000 | 2 | 4485 | 2019 | 1 2019: 4485; 13 2031: 6099.6
Mountain Empire | MountainEmpireAltEd | Electrical | Campo High | Fluorescent CR Lighting |  | 1920 | 4 | 20 | Yes | 2000 | 2 | 7680 | 2019 | 1 2019: 7680
Mountain Empire | MountainEmpireAltEd | Electrical | Office | Fluorescent CR Lighting |  | 2000 | 4 | 20 | No | 1995 | 2 | 8000 | 2019 | 1 2019: 8000
Mountain Empire | MountainEmpireAltEd | Electrical | Book Room | Fluorescent CR Lighting |  | 2000 | 4 | 20 | No | 1995 | 2 | 8000 | 2019 | 1 2019: 8000
Mountain Empire | MountainEmpireAltEd | Electrical | Restroom | Fluorescent CR Lighting |  | 460 | 4 | 20 | Yes | 2000 | 2 | 1840 | 2019 | 1 2019: 1840
Mountain Empire | MountainEmpireAltEd | Plumbing | Campo High | DCW/Sewer |  | 1920 | 18 | 30 | Yes | 2000 | 3 | 34560 | 2030 | 12 2030: 45964.8
Mountain Empire | MountainEmpireAltEd | Plumbing | Office | DCW/Sewer |  | 2000 | 18 | 30 | No | 1945 | 3 | 36000 | 2019 | 1 2019: 36000
Mountain Empire | MountainEmpireAltEd | Plumbing | Book Room | DCW/Sewer |  | 2000 | 18 | 30 | No | 1945 | 3 | 36000 | 2019 | 1 2019: 36000
Mountain Empire | MountainEmpireAltEd | Plumbing | Restroom | DCW/Sewer |  | 460 | 18 | 30 | Yes | 2000 | 3 | 8280 | 2030 | 12 2030: 11012.4
Mountain Empire | MountainEmpireAltEd | Fencing | Perimeter Fence | 2" Chain Link, Galv, 6' |  | 1629 | 22.5 | 15 | No | 2000 | 3 | 36652.5 | 2019 | 1 2019: 36652.5; 16 2034: 53146.125
Mountain Empire | MountainEmpireAltEd | Fencing | Well Fence | 2" Chain Link, Galv, 6' |  | 107 | 22.5 | 15 | No | 2000 | 3 | 2407.5 | 2019 | 1 2019: 2407.5; 16 2034: 3490.875
Mountain Empire | MountainEmpireAltEd | Fencing | Parking Lot Fence | 2" Chain Link, Galv, 6' |  | 33 | 22.5 | 15 | No | 2000 | 3 | 742.5 | 2019 | 1 2019: 742.5; 16 2034: 1076.625
Mountain Empire | MountainEmpireAltEd | Fencing | Campo High Fence | 2" Chain Link, Galv, 6' |  | 200 | 22.5 | 15 | No | 2000 | 3 | 4500 | 2019 | 1 2019: 4500; 16 2034: 6525

## Charts and Graphs
575090

## MountainEmpire Summary
Total SqFt | 180140 |  | Cost per SF New Construction | 350
CRV | 63049000
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
Electrical | 447320 | 602043.24 | 62624.8 | 72594 | 21504 | 51644.2 | 12390 | 9292.8 | 0 | 0 | 32032 | 201495 | 57120 | 14595 | 71710 | 39875 | 0 | 68976.8 | 0 | 0 | 1765216.84
Fencing | 427803.75 | 37504.875 | 0 | 0 | 0 | 0 | 0 | 0 | 21231.9 | 0 | 0 | 0 | 0 | 0 | 0 | 594476.4375 | 53890.5 | 0 | 0 | 0 | 1134907.4625
Finishes | 2026430 | 0 | 68446.32 | 9623.392 | 0 | 69864.8 | 23090.24 | 267503.049 | 4836 | 0 | 659233.965 | 21014 | 76024.34 | 12272.032 | 5538 | 1674234.09 | 15107.84 | 100602.24 | 14414.4 | 0 | 5048234.708
HVAC | 913750 | 9012.5 | 38160 | 0 | 0 | 869400 | 0 | 0 | 119350 | 0 | 0 | 0 | 32640 | 0 | 248500 | 1252437.5 | 12950 | 54360 | 0 | 0 | 3550560
LowVoltage | 240000 | 206000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232000 | 0 | 0 | 0 | 0 | 678000
Paving | 1998897.6 | 51272.8335 | 0 | 0 | 0 | 109844.665 | 58739.751 | 0 | 0 | 0 | 124172.23 | 66206.6685 | 0 | 0 | 0 | 138499.795 | 73673.586 | 0 | 0 | 0 | 2621307.129
Playground | 175426.65 | 0 | 0 | 152447.4 | 0 | 201740.6475 | 0 | 0 | 0 | 0 | 228054.645 | 0 | 0 | 194405.4 | 0 | 254368.6425 | 0 | 0 | 0 | 0 | 1206443.385
Plumbing | 1761344 | 486619.38 | 121501.44 | 113011.2 | 77414.4 | 19872 | 101952 | 0 | 0 | 0 | 1625 | 321753.6 | 168789.6 | 60048 | 122688 | 224512.2 | 0 | 104371.2 | 0 | 0 | 3685502.02
Roofing | 2452592.5 | 107069.53 | 85780.5 | 0 | 22780.8 | 0 | 218854.6 | 113044.25 | 34893.6 | 206267.05 | 243417.2 | 96657.085 | 77928 | 23310.3 | 49629 | 983540.075 | 110024.68 | 0 | 0 | 0 | 4825789.17
Total | 10443564.5 | 1499522.3585 | 376513.06 | 347675.992 | 121699.2 | 1322366.3125 | 415026.591 | 389840.099 | 180311.5 | 206267.05 | 1288535.04 | 707126.3535 | 412501.94 | 304630.732 | 498065 | 5393943.74 | 265646.606 | 328310.24 | 14414.4 | 0 | 24515960.7145
Condition Index | 0.20705
Summary by Priority
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
1 | 3308371.45 | 0 | 0 | 0 | 0 | 68993.33 | 0 | 0 | 0 | 0 | 340510.885 | 0 | 22100 | 0 | 0 | 367642.715 | 0 | 0 | 0 | 0 | 4107619.38
2 | 2259688.05 | 76662.9 | 146734.74 | 0 | 0 | 35772.1875 | 0 | 260301.129 | 0 | 0 | 201223.295 | 0 | 12464.4 | 0 | 20746.2 | 941811.4675 | 0 | 86831.04 | 0 | 0 | 4042237.409
3 | 4875505 | 1422859.4585 | 229778.32 | 347675.992 | 121699.2 | 1217600.795 | 415026.591 | 129538.97 | 180311.5 | 206267.05 | 746800.86 | 707126.3535 | 377937.54 | 304630.732 | 477318.8 | 4084489.5575 | 265646.606 | 241479.2 | 14414.4 | 0 | 16366109.9255
Total | 10443564.5 | 1499522.3585 | 376513.06 | 347675.992 | 121699.2 | 1322366.3125 | 415026.591 | 389840.099 | 180311.5 | 206267.05 | 1288535.04 | 707126.3535 | 412501.94 | 304630.732 | 498065 | 5393943.74 | 265646.606 | 328310.24 | 14414.4 | 0 | 24515960.7145
Summary by Priority - 5 Year
| 1 | 2 | 3 | 4 | 5
| 2019 | 2020 | 2021 | 2022 | 2023 | Total
1 | 3308371.45 | 0 | 0 | 0 | 0 | 3308371.45
2 | 2259688.05 | 76662.9 | 146734.74 | 0 | 0 | 2483085.69
3 | 4875505 | 1422859.4585 | 229778.32 | 347675.992 | 121699.2 | 6997517.9705
Total | 10443564.5 | 1499522.3585 | 376513.06 | 347675.992 | 121699.2 | 12788975.1105
Summary by Building Type
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
Permanent Construction | 8100920.4 | 1263806.8585 | 0 | 158547.912 | 14095.2 | 458301.45 | 219290.551 | 260301.129 | 140581.9 | 0 | 991031.145 | 165570.3035 | 22100 | 202184.952 | 266370.7 | 3885576.2375 | 260010.766 | 0 | 0 | 0 | 16408689.5045
Portable/Modular | 2342644.1 | 235715.5 | 376513.06 | 189128.08 | 107604 | 864064.8625 | 195736.04 | 129538.97 | 39729.6 | 206267.05 | 297503.895 | 541556.05 | 390401.94 | 102445.78 | 231694.3 | 1508367.5025 | 5635.84 | 328310.24 | 14414.4 | 0 | 8107271.21
Total | 10443564.5 | 1499522.3585 | 376513.06 | 347675.992 | 121699.2 | 1322366.3125 | 415026.591 | 389840.099 | 180311.5 | 206267.05 | 1288535.04 | 707126.3535 | 412501.94 | 304630.732 | 498065 | 5393943.74 | 265646.606 | 328310.24 | 14414.4 | 0 | 24515960.7145
Summary by School Site
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
Campo | 2111676.95 | 735896.375 | 41518.08 | 175141.2 | 0 | 159298.5175 | 36670.27 | 9292.8 | 14870.7 | 0 | 384063.355 | 41331.745 | 77928 | 0 | 0 | 1718064.4725 | 45993.22 | 220894.88 | 0 | 0 | 5772640.565
CloverFlat | 577407.6 | 150467.7045 | 20860.8 | 0 | 18396 | 213593.9275 | 116979.477 | 40383.75 | 6361.2 | 33655 | 112904.805 | 257195.5995 | 81926.4 | 0 | 57318.3 | 481677.82 | 16901.822 | 18120 | 0 | 0 | 2204150.2055
Descanso | 660498 | 129585.639 | 0 | 0 | 10752 | 123524.95 | 53852.604 | 7201.92 | 0 | 93884.75 | 98140.77 | 125475.924 | 59633.28 | 0 | 123980.2 | 444902.195 | 64669.044 | 20584.32 | 0 | 0 | 2016685.596
Jacumba | 395744.3 | 72290.55 | 0 | 9623.392 | 0 | 96305.715 | 34479.6 | 0 | 0 | 0 | 67086.63 | 92321.95 | 6364.8 | 35582.332 | 0 | 219044.685 | 12007.24 | 0 | 14414.4 | 0 | 1055265.594
MountainEmpireAltEd | 371673.3 | 35457.75 | 0 | 0 | 0 | 4809.07 | 12045.44 | 0 | 0 | 0 | 17877.34 | 77991.2 | 6099.6 | 0 | 0 | 242673.885 | 15107.84 | 0 | 0 | 0 | 783735.425
MountainEmpireHS | 4803423.6 | 332976.34 | 127697.14 | 0 | 77414.4 | 83810.4475 | 79437.6 | 260301.129 | 119350 | 0 | 405506.14 | 31726.485 | 96886.4 | 0 | 248500 | 1422216.4775 | 110967.44 | 0 | 0 | 0 | 8200213.599
PineValley | 715560.6 | 0 | 0 | 0 | 8685.6 | 226376.0625 | 0 | 0 | 0 | 0 | 87470.305 | 60202.45 | 8101.86 | 0 | 11012.1 | 211220.4125 | 0 | 0 | 0 | 0 | 1328629.39
Potrero | 807580.15 | 42848 | 186437.04 | 162911.4 | 6451.2 | 414647.6225 | 81561.6 | 72660.5 | 39729.6 | 78727.3 | 115485.695 | 20881 | 75561.6 | 269048.4 | 57254.4 | 654143.7925 | 0 | 68711.04 | 0 | 0 | 3154640.34
MOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 10443564.5 | 1499522.3585 | 376513.06 | 347675.992 | 121699.2 | 1322366.3125 | 415026.591 | 389840.099 | 180311.5 | 206267.05 | 1288535.04 | 707126.3535 | 412501.94 | 304630.732 | 498065 | 5393943.74 | 265646.606 | 328310.24 | 14414.4 | 0 | 24515960.7145
MountainEmpireHS
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
Electrical | 71952 | 266090.2 | 12953.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350995.4
Fencing | 123682.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179339.625 | 0 | 0 | 0 | 0 | 303022.125
Finishes | 976242.45 | 0 | 0 | 0 | 0 | 0 | 0 | 260301.129 | 0 | 0 | 324738.895 | 0 | 22100 | 0 | 0 | 426721.66 | 0 | 0 | 0 | 0 | 2010104.134
HVAC | 347250 | 9012.5 | 0 | 0 | 0 | 13800 | 0 | 0 | 119350 | 0 | 0 | 0 | 0 | 0 | 248500 | 431012.5 | 12950 | 0 | 0 | 0 | 1181875
LowVoltage | 20000 | 41200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29000 | 0 | 0 | 0 | 0 | 90200
Paving | 929681.65 | 0 | 0 | 0 | 0 | 70010.4475 | 0 | 0 | 0 | 0 | 79142.245 | 0 | 0 | 0 | 0 | 88274.0425 | 0 | 0 | 0 | 0 | 1167108.385
Plumbing | 1198340 | 0 | 28963.44 | 0 | 77414.4 | 0 | 20390.4 | 0 | 0 | 0 | 1625 | 0 | 74786.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1401519.64
Roofing | 1136275 | 16673.64 | 85780.5 | 0 | 0 | 0 | 59047.2 | 0 | 0 | 0 | 0 | 31726.485 | 0 | 0 | 0 | 267868.65 | 98017.44 | 0 | 0 | 0 | 1695388.915
Total | 4803423.6 | 332976.34 | 127697.14 | 0 | 77414.4 | 83810.4475 | 79437.6 | 260301.129 | 119350 | 0 | 405506.14 | 31726.485 | 96886.4 | 0 | 248500 | 1422216.4775 | 110967.44 | 0 | 0 | 0 | 8200213.599
FCI | 0.29146
Campo
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
Electrical | 112668 | 229690 | 0 | 62130 | 0 | 39569.2 | 0 | 9292.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39875 | 0 | 57380 | 0 | 0 | 550605
Fencing | 93825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14870.7 | 0 | 0 | 0 | 0 | 0 | 0 | 110207.25 | 0 | 0 | 0 | 0 | 218902.95
Finishes | 402731 | 0 | 16078.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145932.67 | 0 | 0 | 0 | 0 | 466428.895 | 0 | 22903.68 | 0 | 0 | 1054074.325
HVAC | 321250 | 0 | 25440 | 0 | 0 | 41400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465812.5 | 0 | 36240 | 0 | 0 | 890142.5
LowVoltage | 60000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29000 | 0 | 0 | 0 | 0 | 89000
Paving | 455565 | 32008.795 | 0 | 0 | 0 | 0 | 36670.27 | 0 | 0 | 0 | 0 | 41331.745 | 0 | 0 | 0 | 0 | 45993.22 | 0 | 0 | 0 | 611569.03
Plumbing | 0 | 468820.98 | 0 | 113011.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224512.2 | 0 | 104371.2 | 0 | 0 | 910715.58
Roofing | 597525.5 | 5376.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149584.5 | 0 | 77928 | 0 | 0 | 283465.575 | 0 | 0 | 0 | 0 | 1113880.175
Total | 2043564.5 | 735896.375 | 41518.08 | 175141.2 | 0 | 80969.2 | 36670.27 | 9292.8 | 14870.7 | 0 | 295517.17 | 41331.745 | 77928 | 0 | 0 | 1619301.42 | 45993.22 | 220894.88 | 0 | 0 | 5438889.56
FCI | 0.28125
PineValley
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
Electrical | 109980 | 0 | 0 | 0 | 0 | 12075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122055
Fencing | 28552.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41401.125 | 0 | 0 | 0 | 0 | 69953.625
Finishes | 108171.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39215.93 | 0 | 8101.86 | 0 | 0 | 104469.6 | 0 | 0 | 0 | 0 | 259958.74
HVAC | 0 | 0 | 0 | 0 | 0 | 165600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165600
LowVoltage | 60000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29000 | 0 | 0 | 0 | 0 | 89000
Paving | 50745.75 | 0 | 0 | 0 | 0 | 7383.8625 | 0 | 0 | 0 | 0 | 8346.975 | 0 | 0 | 0 | 0 | 9310.0875 | 0 | 0 | 0 | 0 | 75786.675
Plumbing | 157878 | 0 | 0 | 0 | 0 | 19872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177750
Roofing | 181585 | 0 | 0 | 0 | 8685.6 | 0 | 0 | 0 | 0 | 0 | 15665 | 60202.45 | 0 | 0 | 11012.1 | 0 | 0 | 0 | 0 | 0 | 277150.15
Total | 696912.6 | 0 | 0 | 0 | 8685.6 | 204930.8625 | 0 | 0 | 0 | 0 | 63227.905 | 60202.45 | 8101.86 | 0 | 11012.1 | 184180.8125 | 0 | 0 | 0 | 0 | 1237254.19
FCI | 0.33617
Jacumba
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
Electrical | 0 | 22734.16 | 0 | 0 | 0 | 0 | 12390 | 0 | 0 | 0 | 0 | 39235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74359.16
Fencing | 25605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37127.25 | 0 | 0 | 0 | 0 | 62732.25
Finishes | 45173.2 | 0 | 0 | 9623.392 | 0 | 0 | 11044.8 | 0 | 0 | 0 | 10760.1 | 0 | 6364.8 | 12272.032 | 0 | 46713.49 | 0 | 0 | 14414.4 | 0 | 156366.214
HVAC | 37500 | 0 | 0 | 0 | 0 | 55200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54375 | 0 | 0 | 0 | 0 | 147075
LowVoltage | 20000 | 41200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29000 | 0 | 0 | 0 | 0 | 90200
Paving | 114476.75 | 0 | 0 | 0 | 0 | 6224.6625 | 0 | 0 | 0 | 0 | 7036.575 | 0 | 0 | 0 | 0 | 7848.4875 | 0 | 0 | 0 | 0 | 135586.475
Plumbing | 62964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48358.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111322.8
Roofing | 59694 | 8356.39 | 0 | 0 | 0 | 0 | 11044.8 | 0 | 0 | 0 | 9859.2 | 4728.15 | 0 | 23310.3 | 0 | 0 | 12007.24 | 0 | 0 | 0 | 129000.08
Total | 365412.95 | 72290.55 | 0 | 9623.392 | 0 | 61424.6625 | 34479.6 | 0 | 0 | 0 | 27655.875 | 92321.95 | 6364.8 | 35582.332 | 0 | 175064.2275 | 12007.24 | 0 | 14414.4 | 0 | 906641.979
FCI | 0.28629
Potrero
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
Electrical | 63440 | 1648 | 41530.8 | 10464 | 6451.2 | 0 | 0 | 0 | 0 | 0 | 32032 | 11305 | 28560 | 14595 | 14910 | 0 | 0 | 0 | 0 | 0 | 224936
Fencing | 52402.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75983.625 | 0 | 0 | 0 | 0 | 128386.125
Finishes | 163718 | 0 | 52368.24 | 0 | 0 | 42191.2 | 0 | 0 | 4836 | 0 | 44713.5 | 0 | 0 | 0 | 5538 | 240715.95 | 0 | 68711.04 | 0 | 0 | 622791.93
HVAC | 36000 | 0 | 0 | 0 | 0 | 358800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52200 | 0 | 0 | 0 | 0 | 447000
LowVoltage | 20000 | 41200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29000 | 0 | 0 | 0 | 0 | 90200
Paving | 215474.65 | 0 | 0 | 0 | 0 | 13656.4225 | 0 | 0 | 0 | 0 | 15437.695 | 0 | 0 | 0 | 0 | 17218.9675 | 0 | 0 | 0 | 0 | 261787.735
Plumbing | 34560 | 0 | 92538 | 0 | 0 | 0 | 81561.6 | 0 | 0 | 0 | 0 | 9576 | 47001.6 | 60048 | 36806.4 | 0 | 0 | 0 | 0 | 0 | 362091.6
Roofing | 221985 | 0 | 0 | 0 | 0 | 0 | 0 | 72660.5 | 34893.6 | 78727.3 | 23302.5 | 0 | 0 | 0 | 0 | 239025.25 | 0 | 0 | 0 | 0 | 670594.15
Total | 807580.15 | 42848 | 186437.04 | 10464 | 6451.2 | 414647.6225 | 81561.6 | 72660.5 | 39729.6 | 78727.3 | 115485.695 | 20881 | 75561.6 | 74643 | 57254.4 | 654143.7925 | 0 | 68711.04 | 0 | 0 | 2807787.54
FCI | 0.22944
CloverFlat
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
Electrical | 63760 | 38501.4 | 8140.8 | 0 | 4300.8 | 0 | 0 | 0 | 0 | 0 | 0 | 81130 | 28560 | 0 | 14910 | 0 | 0 | 0 | 0 | 0 | 239303
Fencing | 59433.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6361.2 | 0 | 0 | 0 | 0 | 0 | 0 | 86178.9375 | 0 | 0 | 0 | 0 | 151973.8875
Finishes | 142264 | 0 | 0 | 0 | 0 | 27673.6 | 0 | 0 | 0 | 0 | 29328 | 0 | 6364.8 | 0 | 0 | 201677.6 | 0 | 0 | 0 | 0 | 407308
HVAC | 84000 | 0 | 12720 | 0 | 0 | 151800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121800 | 0 | 18120 | 0 | 0 | 388440
LowVoltage | 20000 | 41200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29000 | 0 | 0 | 0 | 0 | 90200
Paving | 0 | 11762.7545 | 0 | 0 | 0 | 0 | 13475.777 | 0 | 0 | 0 | 0 | 15188.7995 | 0 | 0 | 0 | 0 | 16901.822 | 0 | 0 | 0 | 57329.153
Plumbing | 80640 | 17798.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160876.8 | 47001.6 | 0 | 24537.6 | 0 | 0 | 0 | 0 | 0 | 330854.4
Roofing | 97640 | 41205.15 | 0 | 0 | 14095.2 | 0 | 103503.7 | 40383.75 | 0 | 33655 | 45006 | 0 | 0 | 0 | 17870.7 | 0 | 0 | 0 | 0 | 0 | 393359.5
Total | 547737.75 | 150467.7045 | 20860.8 | 0 | 18396 | 179473.6 | 116979.477 | 40383.75 | 6361.2 | 33655 | 74334 | 257195.5995 | 81926.4 | 0 | 57318.3 | 438656.5375 | 16901.822 | 18120 | 0 | 0 | 2058767.9405
FCI | 0.17114
Descanso
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
Electrical | 0 | 43379.48 | 0 | 0 | 10752 | 0 | 0 | 0 | 0 | 0 | 0 | 69825 | 0 | 0 | 41890 | 0 | 0 | 11596.8 | 0 | 0 | 177443.28
Fencing | 0 | 37504.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53890.5 | 0 | 0 | 0 | 91395.375
Finishes | 143107 | 0 | 0 | 0 | 0 | 0 | 0 | 7201.92 | 0 | 0 | 52103.87 | 0 | 26993.28 | 0 | 0 | 142603.295 | 0 | 8987.52 | 0 | 0 | 380996.885
HVAC | 63750 | 0 | 0 | 0 | 0 | 82800 | 0 | 0 | 0 | 0 | 0 | 0 | 32640 | 0 | 0 | 92437.5 | 0 | 0 | 0 | 0 | 271627.5
LowVoltage | 20000 | 41200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29000 | 0 | 0 | 0 | 0 | 90200
Paving | 143310 | 7501.284 | 0 | 0 | 0 | 7760.2 | 8593.704 | 0 | 0 | 0 | 8772.4 | 9686.124 | 0 | 0 | 0 | 9784.6 | 10778.544 | 0 | 0 | 0 | 206186.856
Plumbing | 154962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45964.8 | 0 | 0 | 61344 | 0 | 0 | 0 | 0 | 0 | 262270.8
Roofing | 106704 | 0 | 0 | 0 | 0 | 0 | 45258.9 | 0 | 0 | 93884.75 | 0 | 0 | 0 | 0 | 20746.2 | 129512.55 | 0 | 0 | 0 | 0 | 396106.4
Total | 631833 | 129585.639 | 0 | 0 | 10752 | 90560.2 | 53852.604 | 7201.92 | 0 | 93884.75 | 60876.27 | 125475.924 | 59633.28 | 0 | 123980.2 | 403337.945 | 64669.044 | 20584.32 | 0 | 0 | 1876227.096
FCI | 0.19996
MountainEmpireAltEd
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | Total
Electrical | 25520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25520
Fencing | 44302.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64238.625 | 0 | 0 | 0 | 0 | 108541.125
Finishes | 45023 | 0 | 0 | 0 | 0 | 0 | 12045.44 | 0 | 0 | 0 | 12441 | 21014 | 6099.6 | 0 | 0 | 44903.6 | 15107.84 | 0 | 0 | 0 | 156634.48
HVAC | 24000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34800 | 0 | 0 | 0 | 0 | 58800
LowVoltage | 20000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29000 | 0 | 0 | 0 | 0 | 49000
Paving | 89643.8 | 0 | 0 | 0 | 0 | 4809.07 | 0 | 0 | 0 | 0 | 5436.34 | 0 | 0 | 0 | 0 | 6063.61 | 0 | 0 | 0 | 0 | 105952.82
Plumbing | 72000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56977.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128977.2
Roofing | 51184 | 35457.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63668.05 | 0 | 0 | 0 | 0 | 150309.8
Total | 371673.3 | 35457.75 | 0 | 0 | 0 | 4809.07 | 12045.44 | 0 | 0 | 0 | 17877.34 | 77991.2 | 6099.6 | 0 | 0 | 242673.885 | 15107.84 | 0 | 0 | 0 | 783735.425
FCI | 0.27376
0.25868
88641 | 180 | 12126088.8 | 24.15%
Priority 1 By Component By School
1 | Descanso | Campo | CloverFlat | MountainEmpireHS | PineValley | Potrero | Jacumba | MountainEmpireAltEd
Electrical | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fencing | 0 | 17820 | 0 | 0 | 0 | 0 | 0 | 0
Finishes | 0 | 0 | 0 | 645827.65 | 3430.1 | 0 | 0 | 0
HVAC | 0 | 0 | 0 | 0 | 0 | 24000 | 0 | 0
LowVoltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Paving | 130417.15 | 455565 | 0 | 905920.85 | 44325 | 173069.65 | 114476.75 | 89643.8
Plumbing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roofing | 9870 | 104171 | 0 | 441545.5 | 70225 | 26880 | 0 | 51184
Playground | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 140287.15 | 577556 | 0 | 1993294 | 117980.1 | 223949.65 | 114476.75 | 140827.8 | 3308371.45
2 | Descanso | Campo | CloverFlat | MountainEmpireHS | PineValley | Potrero | Jacumba | MountainEmpireAltEd
Electrical | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25520
Fencing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Finishes | 143107 | 0 | 0 | 311174.8 | 0 | 163718 | 0 | 45023
HVAC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24000
LowVoltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 3546848
Paving | 0 | 0 | 0 | 0 | 0 | 42405 | 0 | 0 |  |  |  | 1499124.45
Plumbing | 0 | 0 | 0 | 647532 | 0 | 0 | 0 | 0 |  |  |  | 5239432.7
Roofing | 0 | 363664.5 | 33495 | 209633.5 | 34545 | 177180 | 7584 | 0
Playground | 0 | 31106.25 | 0 | 0 | 0 | 0 | 0 | 0
Total | 143107 | 394770.75 | 33495 | 1168340.3 | 34545 | 383303 | 7584 | 94543 | 2259688.05 | -760563.6
3 | Descanso | Campo | CloverFlat | MountainEmpireHS | PineValley | Potrero | Jacumba | MountainEmpireAltEd
Electrical | 0 | 112668 | 63760 | 71952 | 109980 | 63440 | 0 | 0
Fencing | 0 | 76005 | 59433.75 | 123682.5 | 28552.5 | 52402.5 | 25605 | 44302.5
Finishes | 0 | 402731 | 142264 | 19240 | 104741.25 | 0 | 45173.2 | 0
HVAC | 63750 | 321250 | 84000 | 347250 | 0 | 12000 | 37500 | 0
LowVoltage | 20000 | 60000 | 20000 | 20000 | 60000 | 20000 | 20000 | 20000
Paving | 12892.85 | 0 | 0 | 23760.8 | 6420.75 | 0 | 0 | 0
Plumbing | 154962 | 0 | 80640 | 550808 | 157878 | 34560 | 62964 | 72000
Roofing | 96834 | 129690 | 64145 | 485096 | 76815 | 17925 | 52110 | 0
Playground | 28665 | 37006.2 | 29669.85 | 0 | 18648 | 0 | 30331.35 | 0
Total | 377103.85 | 1139350.2 | 543912.6 | 1641789.3 | 563035.5 | 200327.5 | 273683.55 | 136302.5 | 4875505 | 363927.7 |  | Total Assessed Valuation | 954443030
[9 empty] | 10443564.5 |  |  | Bonding Capacity (2.5%) | 23861075.75
1 | Campo | CloverFlat | Descanso | Jacumba | MountainEmpireAltEd | MountainEmpireHS | PineValley | Potrero | Total
Electrical | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fencing | 17820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17820
Finishes | 0 | 0 | 0 | 0 | 0 | 645827.65 | 3430.1 | 0 | 649257.75
HVAC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24000 | 24000
LowVoltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Paving | 455565 | 0 | 130417.15 | 114476.75 | 89643.8 | 905920.85 | 44325 | 173069.65 | 1913418.2
Plumbing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roofing | 104171 | 0 | 9870 | 0 | 51184 | 441545.5 | 70225 | 26880 | 703875.5
Total | 577556 | 0 | 140287.15 | 114476.75 | 140827.8 | 1993294 | 117980.1 | 223949.65 | 3308371.45

## Districts
Districts | Alpine | JamulDulzura | Mountain Empire
JamulDulzura | Boulder Oaks | Jamul Primary
Alpine | Joan MacQueen | Jamul Intermediate
Mountain Empire | Alpine | Oak Grove Middle School
Creekside
Shadow Hills

## Systems
System | Division | Component | Longevity | Cost Per Unit | Sub Division | Unit | Is Portable | Condition
Electrical | Div 26 | Panel 225A 208/120 3P | 30 | 10500 |  |  | Yes | 1 | 1" Chain Link, Galv, 10' | ChainLink
Electrical | Div 26 | Panel 125A 120/240 1P | 30 | 9000 |  |  | No | 2 | 1" Chain Link, Galv, 6' | ChainLink
Electrical | Div 26 | Panel 225A 480/277 3P | 30 | 12500 |  |  |  | 3 | 1" Chain Link, Galv, 8' | ChainLink
Electrical | Div 26 | Panel 400A 208/120 3P | 30 | 13500 |  |  |  |  | 16ga Iron Fence 10' | Iron
Electrical | Div 26 | Light Standard 10-20' | 25 | 7500 |  |  |  |  | 16ga Iron Fence 6' | Iron
Electrical | Div 26 | Light Standard 20-30' | 25 | 10000 |  |  |  |  | 16ga Iron Fence 8' | Iron
Electrical | Div 26 | Light Standard 30-40' | 25 | 12500 |  |  |  |  | 2" Chain Link, Galv, 10' | ChainLink
Electrical | Div 26 | Fluorescent CR Lighting | 20 | 4 |  |  |  |  | 2" Chain Link, Galv, 4' | ChainLink
Electrical | Div 26 | LED CR Lighting | 20 | 12 |  |  |  |  | 2" Chain Link, Galv, 6' | ChainLink
Fencing | Div 32 | 1" Chain Link, Galv, 10' | 15 | 40 |  |  |  |  | 2" Chain Link, Galv, 8' | ChainLink
Fencing | Div 32 | 1" Chain Link, Galv, 6' | 15 | 27.5 |  |  |  |  | 2" Chain Link, Vinyl Coated, 10' | ChainLink
Finishes | Div 09 | Carpet Tile | 10 | 8.25 |  |  |  |  | 2" Chain Link, Vinyl Coated, 6' | ChainLink
Finishes | Div 09 | Carpet Roll | 15 | 7.9 |  |  |  |  | 2" Chain Link, Vinyl Coated, 8' | ChainLink
Finishes | Div 09 | Linoleum Sheet | 12 | 11.25 |  |  |  |  | Artificial Turf | Turf
Finishes | Div 09 | Rubber Gym | 12 | 15.75 |  |  |  |  | Artificial Turf | Surfacing
Finishes | Div 09 | Rubber Sheet | 12 | 13.5 |  |  |  |  | Ashpalt Shingle | Shingle/Tile
Finishes | Div 09 | Rubber Tile | 12 | 12 |  |  |  |  | Asphalt Parking Lot | ACPaving
Finishes | Div 09 | VAT 9x9 | 20 | 100 |  |  |  |  | Asphalt Playground | ACPaving
Finishes | Div 09 | VCT 12x12 | 20 | 6.15 |  |  |  |  | Boiler | Boiler
Finishes | Div 09 | Vinyl Gym | 10 | 13 |  |  |  |  | BUR - 2ply Torch | BUR
Finishes | Div 09 | Vinyl Sheet | 12 | 9.75 |  |  |  |  | BUR - Emulsion Cap | BUR
Finishes | Div 09 | Vinyl Tile | 12 | 6.5 |  |  |  |  | BUR - Gran Cap | BUR
Finishes | Div 09 | Wood - Court | 15 | 25 |  |  |  |  | BUR - Gravel | BUR
Finishes | Div 09 | Wood - Stage | 15 | 12 |  |  |  |  | Carpet Tile | CarpetTile
Finishes | Div 09 | Paint Exterior | 10 | 1.6 |  |  |  |  | Carpet Roll | CarpetRoll
Finishes | Div 09 | Paint Interior | 10 | 1.5 |  |  |  |  | Chiller | CentralPlant
Finishes | Div 09 | Wall Board | 10 | 3 |  |  |  |  | Clay Tile | Shingle/Tile
Finishes | Div 09 | Geo Tile | 10 | 4.5 |  |  |  |  | Clock/Bell/Paging | CBP
Finishes | Div 09 | Artificial Turf | 10 | 4.25 |  |  |  |  | Composite Shingle | Shingle/Tile
HVAC | Div 23 | Air Handler | 25 | 25000 |  |  |  |  | Condensing Unit | Split
HVAC | Div 23 | Boiler | 25 | 20000 |  |  |  |  | Condensing Unit 1 Ton | Split
HVAC | Div 23 | Chiller | 28 | 20000 |  |  |  |  | Condensing Unit 3 Ton | Split
HVAC | Div 23 | Condensing Unit | 20 | 25000 |  |  |  |  | Condensing Unit 5 Ton | Split
HVAC | Div 23 | Condensing Unit 1 Ton | 10 | 2000 |  |  |  |  | DCW/Sewer | Domestic
HVAC | Div 23 | Condensing Unit 3 Ton | 10 | 6000 |  |  |  |  | Door | Door
HVAC | Div 23 | Condensing Unit 5 Ton | 10 | 10000 |  |  |  |  | EMS | EMS
HVAC | Div 23 | Furnace | 18 | 2500 |  |  |  |  | Fabric/Rope Equipment | Equipment
HVAC | Div 23 | Heat Pump | 15 | 12000 |  |  |  |  | FACP | FireAlarm
HVAC | Div 23 | Heater/Ventilation 100K BTU | 15 | 10000 |  |  |  |  | FACP | FireAlarm
HVAC | Div 23 | Heater/Ventilation 250K BTU | 15 | 20000 |  |  |  |  | FACP FCI 7100 | FireAlarm
HVAC | Div 23 | Multizone | 15 | 65000 |  |  |  |  | FACP FCI 7100 | FireAlarm
HVAC | Div 23 | Package Unit 10 Ton | 15 | 25000 |  |  |  |  | Fire Sprinkler Riser | FireSprinkler
HVAC | Div 23 | Package Unit 2 Ton | 15 | 5000 |  |  |  |  | Fluorescent CR Lighting | Lighting
HVAC | Div 23 | Package Unit 2.5 Ton | 15 | 6250 |  |  |  |  | Furnace | Furnace
HVAC | Div 23 | Package Unit 3 Ton | 15 | 7500 |  |  |  |  | Geo Tile | CarpetTile
HVAC | Div 23 | Package Unit 3.5 Ton | 15 | 8750 |  |  |  |  | Heat Pump | Package
HVAC | Div 23 | Package Unit 4 Ton | 15 | 10000 |  |  |  |  | Heater/Ventilation 100K BTU | Vent
HVAC | Div 23 | Package Unit 5 Ton | 15 | 12500 |  |  |  |  | Heater/Ventilation 250K BTU | Vent
HVAC | Div 23 | Package Unit 7.5 Ton | 15 | 18750 |  |  |  |  | Intrusion | Security
HVAC | Div 23 | Package Unit 30 Ton | 20 | 75000 |  |  |  |  | LED CR Lighting | Lighting
LowVoltage | Div 26 | FACP FCI 7100 | 15 | 15000 |  |  |  |  | Light Standard 10-20' | Lighting
LowVoltage | Div 26 | Clock/Bell/Paging | 20 | 40000 |  |  |  |  | Light Standard 20-30' | Lighting
LowVoltage | Div 26 | Intrusion | 10 | 40000 |  |  |  |  | Light Standard 30-40' | Lighting
LowVoltage | Div 26 | EMS | 15 | 75000 |  |  |  |  | Linoleum Sheet | ResilientSheet
Paving | Div 32 | Asphalt Playground | 30 | 5.5 |  |  |  |  | Metal Equipment | Equipment
Paving | Div 32 | Asphalt Parking Lot | 30 | 7.5 |  |  |  |  | Metal Halide 400W Dual | Lighting
Paving | Div 32 | Seal Coat and Stripe | 5 | 0.35 |  |  |  |  | Metal Halide 400W Single | Lighting
Plumbing | Div 22 | DCW/Sewer | 30 | 18 |  |  |  |  | Multizone | Multizone
Plumbing | Div 22 | Fire Sprinkler Riser | 25 | 50000 |  |  |  |  | Package Unit 10 Ton | Package
Plumbing | Div 22 | Restroom Sink | 30 | 1600 |  |  |  |  | Package Unit 2 Ton | Package
Plumbing | Div 22 | Urinal | 30 | 1100 |  |  |  |  | Package Unit 2.5 Ton | Package
Plumbing | Div 22 | Water Closet | 30 | 1600 |  |  |  |  | Package Unit 20 Ton | Package
Plumbing | Div 22 | Water Heater 10 Gallon Electric | 10 | 1250 |  |  |  |  | Package Unit 25 Ton | Package
Plumbing | Div 22 | Water Heater 100 Gallon Electric | 10 | 5000 |  |  |  |  | Package Unit 3 Ton | Package
Plumbing | Div 22 | Water Heater 30 Gallon Electric | 10 | 2000 |  |  |  |  | Package Unit 3.5 Ton | Package
Plumbing | Div 22 | Water Heater 50 Gallon Electric | 10 | 2500 |  |  |  |  | Package Unit 30 Ton | Package
Roofing | Div 07 | BUR - Gravel | 30 | 18 |  |  |  |  | Package Unit 4 Ton | Package
Roofing | Div 07 | BUR - Gran Cap | 25 | 15 |  |  |  |  | Package Unit 5 Ton | Package
Roofing | Div 07 | BUR - Emulsion Cap | 20 | 13.5 |  |  |  |  | Package Unit 7.5 Ton | Package
Roofing | Div 07 | Poly Foam | 10 | 10 |  |  |  |  | Paint Exterior | PaintExt
Roofing | Div 07 | SP - TPA/PVC | 15 | 15 |  |  |  |  | Paint Interior | PaintInt
Roofing | Div 07 | SP - TPO | 10 | 12 |  |  |  |  | Panel 100A 208/120 3P | Distribution
Roofing | Div 07 | Standing Seam | 25 | 25 |  |  |  |  | Panel 125A 120/240 1P | Distribution
Roofing | Div 07 | Ashpalt Shingle | 15 | 9.5 |  |  |  |  | Panel 175A 208/120 3P | Distribution
Roofing | Div 07 | Composite Shingle | 50 | 25 |  |  |  |  | Panel 200A 208/120 3P | Distribution
Roofing | Div 07 | Clay Tile | 50 | 25 |  |  |  |  | Panel 225A 208/120 3P | Distribution
Roofing | Div 07 | Vinyl Fabric | 10 | 15 |  |  |  |  | Panel 225A 480/277 3P | Distribution
LowVoltage | Div 26 | FACP | 15 | 20000 |  |  |  |  | Panel 400A 208/120 3P | Distribution
Roofing | Div 07 | BUR - 2ply Torch | 10 | 8 |  |  |  |  | Main Switch Board 1600A 208/120 3P 42,000AIC | Distribution
Fencing | Div 32 | 1" Chain Link, Galv, 8' | 15 | 30.5 |  |  |  |  | Plastic Equipment | Equipment
Fencing | Div 32 | 16ga Iron Fence 10' | 25 | 150 |  |  |  |  | Poly Foam | Foam
Fencing | Div 32 | 16ga Iron Fence 6' | 25 | 110 |  |  |  |  | Restroom Sink | Fixture
HVAC | Div 23 | Package Unit 20 Ton | 20 | 50000 |  |  |  |  | Rubber Gym | ResilientSheet
HVAC | Div 23 | Package Unit 25 Ton | 20 | 62500 |  |  |  |  | Rubber Mat | Surfacing
Electrical | Div 26 | Metal Halide 400W Single | 20 | 300 |  |  |  |  | Rubber Pour in Place | Surfacing
Electrical | Div 26 | Metal Halide 400W Dual | 20 | 400 |  |  |  |  | Rubber Sheet | ResilientSheet
Electrical | Div 26 | Main Switch Board 1600A 208/120 3P 42,000AIC | 30 | 145000 |  |  |  |  | Rubber Tile | ResilientTile
Electrical | Div 26 | Panel 100A 208/120 3P | 30 | 8500 |  |  |  |  | Sand | Surfacing
Electrical | Div 26 | Panel 175A 208/120 3P | 30 | 10500 |  |  |  |  | Seal Coat and Stripe | SealMaintenance
Electrical | Div 26 | Panel 200A 208/120 3P | 30 | 10500 |  |  |  |  | Security Camera | Security
Electrical | Div 26 | Panel 150A 120/240 1P | 30 | 8500 |  |  |  |  | SP - TPA/PVC | SinglePly
Electrical | Div 26 | Panel 400A 277/480 3P | 30 | 8500 |  |  |  |  | SP - TPO | SinglePly
Electrical | Div 26 | Panel 225A 277/480 3P | 30 | 8500 |  |  |  |  | Stadium Lighting | Lighting
Plumbing | Div 22 | Water Heater 12 Gallon Electric | 10 | 1250 |  |  |  |  | Standing Seam | Steel
Plumbing | Div 22 | Water Heater 20 Gallon Electric | 10 | 1500 |  |  |  |  | Urinal | Fixture
Plumbing | Div 22 | Water Heater 10 Gallon Gas | 10 | 1250 |  |  |  |  | Urinal Waterless | Fixture
Plumbing | Div 22 | Water Heater 100 Gallon Gas | 10 | 5000 |  |  |  |  | VAT 9x9 | ResilientTile
Plumbing | Div 22 | Water Heater 12 Gallon Electric | 10 | 2000 |  |  |  |  | VCT 12x12 | ResilientTile
Plumbing | Div 22 | Water Heater 20 Gallon Gas | 10 | 2500 |  |  |  |  | Vinyl Fabric | VinylFabric
Plumbing | Div 22 | Water Heater 30 Gallon Gas | 10 | 1250 |  |  |  |  | Vinyl Gym | ResilientSheet
Plumbing | Div 22 | Water Heater 50 Gallon Gas | 10 | 1500 |  |  |  |  | Vinyl Sheet | ResilientSheet
Plumbing | Div 22 | Water Heater Instahot Electric | 10 | 800 |  |  |  |  | Vinyl Tile | ResilientTile
Plumbing | Div 22 | Water Heater Instahot Gas | 10 | 800 |  |  |  |  | Wall Board | WallTreatment
Fencing | Div 32 | 16ga Iron Fence 8' | 25 | 130 |  |  |  |  | Water Closet | Fixture
Fencing | Div 32 | 2" Chain Link, Galv, 10' | 15 | 35 |  |  |  |  | Water Heater 10 Gallon | WaterHeater
Fencing | Div 32 | 2" Chain Link, Galv, 4' | 15 | 18.75 |  |  |  |  | Water Heater 100 Gallon | WaterHeater
Fencing | Div 32 | 2" Chain Link, Galv, 6' | 15 | 22.5 |  |  |  |  | Water Heater 30 Gallon | WaterHeater
Fencing | Div 32 | 2" Chain Link, Galv, 8' | 15 | 25.5 |  |  |  |  | Water Heater 50 Gallon | WaterHeater
Fencing | Div 32 | 2" Chain Link, Vinyl Coated, 10' | 15 | 45 |  |  |  |  | Window | Window
Fencing | Div 32 | 2" Chain Link, Vinyl Coated, 6' | 15 | 32.5 |  |  |  |  | Wood - Court | Wood
Fencing | Div 32 | 2" Chain Link, Vinyl Coated, 8' | 15 | 35.5 |  |  |  |  | Wood - Stage | Wood
Finishes |  | Custom Exterior | 20 | 6.5 |  |  |  |  | Wood Fiber | Surfacing
Playground |  | Wood Fiber | 5 | 3.15 |  | Cubic Foot |  |  | Panel 150A 120/240 1P | Distribution
Electrical | Div 26 | Panel 100A 277/480 3P | 30 | 8500 |  |  |  |  | Panel 400A 277/480 3P | Distribution
Paving | Div 32 | PC Sidewalk (Reinforced) | 50 | 8.5 |  |  |  |  | Custom Exterior | Custom
Paving | Div 32 | PC Sidewalk (Non-reinforced) | 30 | 6.5
Playground | Div 13 | Rubber Pour in Place | 10 | 30

## CSI Codes
System |  | System | Sub System
Roofing | Div 07 | Electrical | Distribution
Paving | Div 32 | Electrical | Lighting
HVAC | Div 23 | Roofing | BUR
Openings | Div 08 | Roofing | Standing Seam
Finishes | Div 09 | Roofing | Ballast
Plumbing | Div 22 | Roofing | Single Ply
Electrical | Div 26 | Roofing | Shingle/Tile
LowVoltage | Div 26 | Roofing | Foam
Fencing | Div 32 | Openings | Interior Doors
Playground | Div 13 | Openings | Exterior Doors
|  | Openings | Windows
|  | Finishes | Interior Paint
|  | Finishes | Exterior Paint
|  | Finishes | Interior Wall Treatment
|  | Finishes | Carpet Tile
|  | Finishes | Carpet Roll
|  | Finishes | Resilient Tile
|  | Finishes | Resilient Sheet
|  | Finishes | Ceiling Tile
|  | Plumbing | Water Heater
|  | Plumbing | Domestic Cold Water
|  | Plumbing | Sewer
|  | Plumbing | Gas
|  | Plumbing | Fire Sprinkler
|  | LowVoltage | Clock/Bell/Paging
|  | LowVoltage | Fire Alarm
|  | Fencing | Chain Link
|  | Fencing | Iron
|  | Paving | Asphalt Concrete
|  | Paving | Seal Coat/Maintenance
|  | HVAC | Package
|  | HVAC | Boiler
|  | HVAC | Central Plant
|  | HVAC | Multizone
|  | HVAC | Split
|  | HVAC | Furnace

## Roofing
Roofing | Longevity | Sub Class
BUR - Gravel | 30 | BUR
BUR - Gran Cap | 25 | BUR
BUR - Emulsion Cap | 20 | BUR
BUR - 2ply Torch | 10 | BUR
Poly Foam | 10 | Foam
Ashpalt Shingle | 50 | Shingle/Tile
Composite Shingle | 50 | Shingle/Tile
Clay Tile | 50 | Shingle/Tile
SP - TPA/PVC | 20 | SinglePly
SP - TPO | 10 | SinglePly
Standing Seam | 30 | Steel
Vinyl Fabric | 10 | VinylFabric

## Fencing
Fencing
2" Chain Link, Galv, 4' | ChainLink
2" Chain Link, Galv, 6' | ChainLink
2" Chain Link, Galv, 8' | ChainLink
2" Chain Link, Galv, 10' | ChainLink
1" Chain Link, Galv, 6' | ChainLink
1" Chain Link, Galv, 8' | ChainLink
1" Chain Link, Galv, 10' | ChainLink
2" Chain Link, Vinyl Coated, 6' | ChainLink
2" Chain Link, Vinyl Coated, 8' | ChainLink
2" Chain Link, Vinyl Coated, 10' | ChainLink
16ga Iron Fence 6' | Iron
16ga Iron Fence 8' | Iron
16ga Iron Fence 10' | Iron

## Paving
Paving | Longevity | Cost per Unit
Asphalt Playground | 25 | ACPaving
Asphalt Parking Lot | 25 | ACPaving
Seal Coat and Stripe | 5 | SealMaintenance
PC Sidewalk (Reinforced) | 50
PC Sidewalk (Non-reinforced) | 30

## Plumbing
Plumbing
DCW/Sewer | Domestic
Fire Sprinkler Riser | FireSprinkler
Urinal | Fixture
Restroom Sink | Fixture
Urinal Waterless | Fixture
Water Closet | Fixture
Water Heater 10 Gallon Electric | WaterHeater
Water Heater 100 Gallon Electric | WaterHeater
Water Heater 12 Gallon Electric | WaterHeater
Water Heater 20 Gallon Electric | WaterHeater
Water Heater 30 Gallon Electric | WaterHeater
Water Heater 50 Gallon Electric | WaterHeater
Water Heater Instahot Electric | WaterHeater
Water Heater 10 Gallon Gas | WaterHeater
Water Heater 100 Gallon Gas | WaterHeater
Water Heater 12 Gallon Gas | WaterHeater
Water Heater 20 Gallon Gas | WaterHeater
Water Heater 30 Gallon Gas | WaterHeater
Water Heater 50 Gallon Gas | WaterHeater
Water Heater Instahot Gas | WaterHeater

## Electrical
Electrical
FACP | FireAlarm
FACP FCI 7100 | FireAlarm
Fluorescent CR Lighting | Lighting
LED CR Lighting | Lighting
Light Standard 10-20' | Lighting
Light Standard 20-30' | Lighting
Light Standard 30-40' | Lighting
Main Switch Board 1600A 208/120 3P 42,000AIC | Distribution
Metal Halide 400W Dual | Lighting
Metal Halide 400W Single | Lighting
Panel 100A 208/120 3P | Distribution
Panel 125A 120/240 1P | Distribution
Panel 150A 120/240 1P | Distribution
Panel 175A 208/120 3P | Distribution
Panel 200A 208/120 3P | Distribution
Panel 225A 208/120 3P | Distribution
Panel 225A 480/277 3P | Distribution
Panel 400A 208/120 3P | Distribution
Panel 400A 277/480 3P | Distribution
Stadium Lighting | Lighting
Panel 100A 277/480 3P | Distribution

## LowVoltage
Low Voltage
FACP | FireAlarm
FACP FCI 7100 | FireAlarm
Clock/Bell/Paging | CBP
Intrusion | Security
Security Camera | Security
EMS | EMS

## Finishes
Flooring
Artificial Turf | Turf
Carpet Tile | CarpetTile
Carpet Roll | CarpetRoll
Geo Tile | CarpetTile
Linoleum Sheet | ResilientSheet
Paint Exterior | PaintExt
Paint Interior | PaintInt
Rubber Gym | ResilientSheet
Rubber Sheet | ResilientSheet
Rubber Tile | ResilientTile
VAT 9x9 | ResilientTile
VCT 12x12 | ResilientTile
Vinyl Gym | ResilientSheet
Vinyl Sheet | ResilientSheet
Vinyl Tile | ResilientTile
Wall Board | WallTreatment
Wood - Court | Wood
Wood - Stage | Wood
Custom Exterior | Custom

## Openings
Openings
Door | Door
Window | Window

## HVAC
HVAC
Air Handler
Boiler | Boiler
Chiller | CentralPlant
Condensing Unit | Split
Condensing Unit 1 Ton | Split
Condensing Unit 3 Ton | Split
Condensing Unit 5 Ton | Split
Furnace | Furnace
Heat Pump | Package
Multizone | Multizone
Package Unit 2 Ton | Package
Package Unit 2.5 Ton | Package
Package Unit 3 Ton | Package
Package Unit 3.5 Ton | Package
Package Unit 4 Ton | Package
Package Unit 5 Ton | Package
Package Unit 7.5 Ton | Package
Package Unit 10 Ton | Package
Heater/Ventilation 100K BTU | Vent
Heater/Ventilation 250K BTU | Vent
Package Unit 30 Ton | Package
Package Unit 20 Ton | Package
Package Unit 25 Ton | Package

## Playground
Playground
Plastic Equipment | Equipment
Metal Equipment | Equipment
Fabric/Rope Equipment | Equipment
Wood Fiber | Surfacing
Sand | Surfacing
Rubber Mat | Surfacing
Rubber Pour in Place | Surfacing
Artificial Turf | Surfacing

## MEUSD Schools
District | Building | Descanso | Campo | Clover Flat | Mountain Empire HS | Pine Valley | Potrero | Jacumba | Moutain Empire Alt Ed
Jamul Dulzura | Campo | Admin | Athletic Field | Office | Front Parking Lot | Building 1 | MS1 | AC Sidewalk | Campo High
Jamul Dulzura | CloverFlat | Building 1 | Blacktop | AC Playground | Middle Parking Lot | Building 2 | MS2 | ASP | Office
Jamul Dulzura | Descanso | Building 2 | Classroom Building | Admin Fence | North Parking Lot | Building 3 | MS3 | Blacktop | Book Room
| Jacumba | Room 7 | Drop Off Loop | Building 1 | Fire Road | Building 4 | Upper Restroom | Building A | Restroom
| MountainEmpireAltEd | Room 8 | Kinder Playground | Building 10 | North Blacktop | Building 5 | 4Plex | Office | North Parking Lot
| MountainEmpireHS | Room 9 | P1 | Building 12 | Maintenance Road | Building 6 | Building 2 | Parking Lot | South Parking Lot
| PineValley | Room 10 | P2 | Building 2 | East Blacktop | Building 7 | Building 3 | PC Basketball Court | Blacktop
| Potrero | ASP | P3 | Building 3 | Handball Court | Building 8 | Building 4 | Perimeter Fence | Perimeter Fence
|  | Restroom | P4 | Building 4 | Basketball Court | Restroom | Building 5 | Playground | Well Fence
|  | Parking Lot | P5 | Building 7 | District Office Parking Lot | Lunch Shelter | Building 6 | Restroom | Parking Lot Fence
|  | Kinder Blacktop | Parking Lot | Building 8 | MOT Parking | Swings | Building 7 |  | Campo High Fence
|  | Blacktop | Primary Playground | Building 9 | Admin | Playground | Building 8
|  | Quad | Pump House | Cafeteria | S | Parking Lot | Building 9
|  | Primary Playground | Shade Structure | Campus Blacktop | Gym | Blacktop | Building 10
|  | Perimeter Fence | South Wing | Headstart | P1 |  | Building 11
|  | SE Fence | Swings | Headstart Fence | P2 |  | Computer Lab
|  | SW Fence |  | Parking Lot | P3 |  | Speech Center
|  | Building 1C |  | Parking Lot Fence | P4 |  | Lower Restroom
|  |  |  | Pedestrian Fence | P5 |  | Office
|  |  |  | Perimeter Fence | P6 |  | Shade Shelter (North)
|  |  |  | Playground | P7 |  | Shade Shelter (South)
|  |  |  | Restroom | P8 |  | Preschool
|  |  |  | Shade Structure | P9 |  | Primary Playground 1
|  |  |  | Solar Fence | Q1 |  | Primary Playground 2
[5 empty] | L1 |  | East Parking Lot
[5 empty] | L2 |  | Fire Lane
[5 empty] | L3 |  | Kinder Blacktop
[5 empty] | L4 |  | Kinder Playground
[5 empty] | Greenhouse |  | Perimeter Fence
[5 empty] | Mirror Room |  | Parking Lot Fence
[5 empty] | P10 |  | Kinder Fence
[5 empty] | P11 |  | Southeast Fence
[5 empty] | Kitchen |  | Ball Field Fence
West Parking Lot Fence
Well Fence
Playground 1 Fence
Preschool Fence
Main Blacktop
Blacktop/Quad